## READ ME
Commercial HVAC New Construction Database
| Executive Summary | Workbook Contents
|  | Tab Name | Description
|  | READ ME | Project background and general information
|  | Data Dictionary | Definitions of database fields
|  | Stage 1 Project Data | Data Storage Table for all Stage 1 project level information | Data Storage Table for all project level information
|  | Stage 2 Heating | Data Storage Table for primary heating equipment | Data Storage Table for primary heating equipment
|  | Stage 2 Cooling | Data Storage Table for primary cooling equipment | Data Storage Table primary cooling equipment
|  | Stage 2 Supp HVAC | Data Storage Table for supplementary HVAC equipment | Data Storage Table for supplementary HVAC equipment
|  | Stage 2 HRV | Data Storage Table for air-to-air heat recovery equipment | Data Storage Table for Air-to-Air heat recovery equipment
|  | Population Summary | Summarizes the total extrapolated population of commercial new construction conditioned square footage by domain, the extrapolation process, and the relative precision by domain
How to Use this Workbook
Study Manager:
Juan Carlos Blacker
Bonneville Power Administration
jcblacker@bpa.gov
Contributors:
Bretnie Eschenbach, Jessica DeWitt, Lucas Judson, Kate Bushman
Cadeo Group
Faith DeBolt, Michael Baker
SBW Consulting
BPA contracted with Cadeo to develop a data set of commercial HVAC information using permit data from commercial new construction and major renovation building projects completed from 2016 through 2021. BPA will use this data to estimate commercial HVAC electricity consumption in a planned commercial HVAC market model in 2022. The table below summarizes the scope of this commercial HVAC data collection effort.
For more information on the scope, methods, and findings from this data collection effort please refer to the team's Methodology Memo and Lessons Learned Memo.
To collect this permit data, the team developed a representative sample of 300 projects that fell within the scope requirements using a sample frame drawn from a new construction data set purchased from Dodge Data Analytics. The team submitted public records requests with the relevant jurisdiction asking for building plans, mechanical schedules, or energy efficiency code compliance documents. In some cases jurisdictions could not provide these documents and the project had to be replaced with the next relevant project in our sample. For more information about the replacement process and common reasons why certain projects needed to be replaced see the Sampling Plan or Lessons Learned Memo.
The team received the applicable permit files, confirmed that each project met the scope requirements and contained the necessary information for cataloging. In some cases, the team found that permitted projects did not include any new HVAC scope or heating/cooling capacity only after permit documentation was received. The team elected to replace those permitted projects with others from the sample frame in order to ensure adequate data was collected. Because of this, the team collected a total of 382 permitted projects in order to capture the required 300 projects with new HVAC work. The additional permitted projects are considered "oversampled" projects, further defined below.
The team cataloged data in two stages. All in-scope projects received Stage 1 cataloging, which included high level project data (conditioned square footage, completion date, building type, primary heating and cooling system type, etc.). In some cases, buildings had more than one primary HVAC system which the team defined as an HVAC system serving greater than 30% of the relevant square footage. The team then used a modifier with the project ID to catalog each primary system as a unique entry. For example, a restaurant may use one system for the dining area and a separate system for the kitchen. If each system served 50% of the floor area the team would catalog each separately using a modifier as [Project ID - Dining area] and [Project ID - Kitchen].
In Stage 2, the team cataloged detailed HVAC data for projects with primary heating and cooling technologies of interest to BPA (VRF, DHP, ASHP, and ducted cooling systems). Stage 2 data includes detailed HVAC information including system efficiency, capacity, equipment manufacturer and model number, and presence of heat recovery ventilation. For a full list of Stage 1 and Stage 2 collection fields see the data dictionary tab.
Additionally, 66 projects in the sample did not include new HVAC systems, or were not yet completed projects. The database identifies these projects as "oversampled" projects, with square footages and completion dates listed as zero for extrapolation purposes.
The subsequent tabs of this workbook includes the Stage 1 and Stage 2 data cataloged for each project.
All projects in the sample have a unique project identifier which is consistent across tabs. This "Project_ID" can be used to map HVAC equipment to a specific project. For example, the Stage 1 Project Data tab includes general project information, and the heating system or cooling system associated with specific projects in Stage 1 can be found in the corresponding Stage 2 tabs by finding the matching project_ID.
Each project in the sample includes a sample weight used to estimate the project's representativeness in the region. The sample is stratified by building type and east or west of the Cascades. When using this data set, utilize the sample weights to extrapolate data to the region by multiplying the project's square footage by the sample weight. The Population Summary tab includes additional detail on the sample weight development and the relative precision by domain.
The team developed the sample weights using a regression analysis of the square footage recorded during Stage 1 and the sampling plan's Construction Value from the Dodge data set.

## Data Dictionary
Data Dictionary |  |  | Definition of Terms Used in Workbook
Field Name | Tab | Definition | Term or Entry | Where Used | Description
Project ID | Stage1ProjectData | Project ID. Unique ID derived from Dodge Report Number. | " - " | Stage1ProjectData Tab Sq_Ft & Completion_Date | " - " was used to designate no square footage and no completion date for on oversampled projects, which included no new HVAC scope of work.
Project ID Code | Stage1ProjectData | Project ID and any modifiers. Modifiers are descriptions of the sub-areas of a building when two HVAC systems served more than 30% of the conditioned floor area (splitting the project into two primary HVAC systems). Modifiers are only used in these cases and are not intended to be filtered. | "N/A" | Stage2Heating Stage2Cooling Stage2SuppHVAC Stage2HRV | "N/A" was used in cases where a specific field or capability does not apply to that HVAC equipment. For example, "HP Includes Auxiliary Heat?" only applies to heat pump equipment, and is noted as N/A for all other HVAC equipment types.
Stage | Stage1ProjectData | Level of catalog. All projects received Stage 1 cataloging, but only projects with technologies of interest received additional Stage 2 catalog (VRF, DHP, ASHP, and the remaining projects with ducted cooling). Additional "oversample" projects did not receive cataloging after determining the project was not yet complete or did not include new HVAC systems. | (blank) | All Tabs | Fields were left blank when they did not apply to that specific entry or HVAC equipment.
Project_ID_mod | Stage1ProjectData | Project ID modifier, if buildings had more than one primary HVAC system serving greater than 30% of the relevant square footage | "Unknown" | Stage2Heating Stage2Cooling Stage2SuppHVAC Stage2HRV | "Unknown" indicates fields that do apply to the subject project and/or equipment, but the information was not included in the project permit drawings and documentation.
Site_City | Stage1ProjectData | Project city
Site_State | Stage1ProjectData | Project state
Site_Zip | Stage1ProjectData | Project zip code
Sq_ft | Stage1ProjectData | Conditioned square footage. When multiple primary HVAC systems, square footage is split between relevant areas served. Note: Oversample projects (those with no completed HVAC scope) are listed as "-" (zero) square footage for extrapolation purposes.
Completion_Date | Stage1ProjectData | Project completion date. Note: Oversample projects (those with no completed HVAC scope) indicate "-" for completion date.
Construction Type | Stage1ProjectData | Type of Work (new, alteration, renovation, addition as defined by Dodge)
Council_Building_Type | Stage1ProjectData | Northwest Power and Planning Council building type, mapped from Dodge building type
Permit_Jurisdiction | Stage1ProjectData | Listed as the City, State of the permitting jurisdiction (or county where applicable). Only cataloged for Stage 2 projects.
Permit_Code_Cycle | Stage1ProjectData | Applicable energy code cycle (only cataloged for Stage 2 projects)
Compliance_Path | Stage1ProjectData | Prescriptive or performance based energy code compliance (only cataloged for Stage 2 projects)
Efficiency_Opt_1 | Stage1ProjectData | Additional efficient equipment option 1 (only cataloged for Stage 2 projects)
Efficiency_Opt_2 | Stage1ProjectData | Additional efficient equipment option 2 (only cataloged for Stage 2 projects)
Primary_Heating_System | Stage1ProjectData | Primary heating system
Primay_Heat_Other | Stage1ProjectData | Description of "other" primary heating system
Primary_Cooling_System | Stage1ProjectData | Primary cooling system
Primary_Cool_Other | Stage1ProjectData | Description of "other" primary cooling system
Primary_HeatFuel | Stage1ProjectData | Primary heating fuel
Primary_HeatFuel_Other | Stage1ProjectData | Description of "other" heating fuel
SHS_VRF | Stage1ProjectData | Qty of supplemental VRF heating systems
SHS_DHP | Stage1ProjectData | Qty of supplemental DHP heating systems
SHS_PTHP | Stage1ProjectData | Qty of supplemental PTHP heating systems
SHS_ASHP_Packaged | Stage1ProjectData | Qty of supplemental packaged ASHP heating systems
SHS_ASHP_Split | Stage1ProjectData | Qty of supplemental ASHP split system heating systems
SCS_Ductless | Stage1ProjectData | Qty of supplemental DHP cooling systems
SCS_PTAC | Stage1ProjectData | Qty of supplemental PTAC cooling systems
SCS_DXRTU | Stage1ProjectData | Qty of supplemental RTU DX cooling systems
Ventilation_decoupled | Stage1ProjectData | User selects decoupled (Yes) or non-decoupled (No) ventilation
HVAC_include_HRV | Stage1ProjectData | HVAC includes air to air heat/energy recovery?
Notes | Stage1ProjectData | Includes any relevant information that may not be collected elsewhere
Sample_Weight | Stage1ProjectData | The number of projects in the sample that project represents. To calculate the conditioned square footage that project represents, multiply the square footage by the sample weight.
Equipment Type | Stage2Heating | Equipment type
Equipment ID | Stage2Heating | Unique entry ID for each piece of HVAC equipment
Manufacturer | Stage2Heating | Manufacturer
Model | Stage2Heating | Model
Capacity_Metric_1 | Stage2Heating | Capacity 1
Capacity_Metric_1_Units | Stage2Heating | Units of capacity 1
Capacity_Metric_2 | Stage2Heating | Capacity 2
Capacity_Metric_2_Units | Stage2Heating | Units of capacity 2
Efficiency_Metric_1 | Stage2Heating | Efficiency 1
Efficiency_Metric_1_Units | Stage2Heating | Units of efficiency 1
Efficiency_Metric_2 | Stage2Heating | Efficiency 2
Efficiency_Metric_2_Units | Stage2Heating | Units of efficiency 2
Efficiency_Metric_3 | Stage2Heating | Efficiency 3
Efficiency_Metric_3_Units | Stage2Heating | Units of efficiency 3
Fuel Type | Stage2Heating | Heating Fuel Type
Equipment_Type_Other | Stage2Heating | Other equipment type description
Cap_met_other | Stage2Heating | Other capacity
Cap_met_other_units | Stage2Heating | Units of other capacity
Eff_met_other | Stage2Heating | Other efficiency
Eff_met_other_units | Stage2Heating | Units of other efficiency
HP Includes Auxiliary Heat? | Stage2Heating | HP Includes Auxiliary Heat?
Size of Aux Heat | Stage2Heating | Size of Aux Heat
Equipment_Type_short | Stage2Cooling | Equipment type short
Equipment Type | Stage2Cooling | Equipment type
Equipment ID | Stage2Cooling | Unique entry ID for each piece of HVAC equipment
Manufacturer | Stage2Cooling | Manufacturer
Model | Stage2Cooling | Model
Capacity_Metric_1 | Stage2Cooling | Capacity 1
Capacity_Metric_1_Units | Stage2Cooling | Units of capacity 1
Capacity_Metric_2 | Stage2Cooling | Capacity 2
Capacity_Metric_2_Units | Stage2Cooling | Units of capacity 2
Efficiency_Metric_1 | Stage2Cooling | Efficiency 1
Efficiency_Metric_1_Units | Stage2Cooling | Units of efficiency 1
Efficiency_Metric_2 | Stage2Cooling | Efficiency 2
Efficiency_Metric_2_Units | Stage2Cooling | Units of efficiency 2
Fuel Type | Stage2Cooling | Cooling Fuel type
Fan Control | Stage2Cooling | Fan control description. Documents Constant Volume (CV), Variable Air Volume (VAV), or 2-speed fans for packaged/central equipment. Does not apply (N/A) to ductless equipment - VRF, DHP
VRF Heat Recovery? | Stage2Cooling | Includes VRF heat recovery? "N/A" for all non-VRF systems. "Unknown" was used to indicate VRF systems in which the project documentation did not specifically state whether VRF heat recovery was included.
Long Description | Stage2SuppHVAC | Supplementary system description
Equipment ID | Stage2SuppHVAC | Unique entry ID for each piece of HVAC equipment
Cooling Capacity | Stage2SuppHVAC | Capacity 1
Capacity_Metric_1_Units | Stage2SuppHVAC | Units of capacity 1
Cooling Efficiency | Stage2SuppHVAC | Efficiency 1
Efficiency_Metric_1_Units | Stage2SuppHVAC | Units of efficiency 1
Cooling Eff2 | Stage2SuppHVAC | Efficiency 2
Efficiency_Metric_2 | Stage2SuppHVAC | Units of efficiency 2
Heating Capacity | Stage2SuppHVAC | Capacity 1
Heating_Capacity_Metric | Stage2SuppHVAC | Units of capacity 1
Heating Efficiency | Stage2SuppHVAC | Efficiency 1
Efficiency_Metric_Units | Stage2SuppHVAC | Units of efficiency 1
Efficiency_2 | Stage2SuppHVAC | Efficiency 2
Efficiency_Metric_2_Units | Stage2SuppHVAC | Units of efficiency 2
Heating Fuel Type | Stage2SuppHVAC | Heating Fuel type
Cooling Fuel Type | Stage2SuppHVAC | Cooling Fuel type
Includes_AuxElecCoils | Stage2SuppHVAC | Includes auxiliary electric coils?
AuxElecCoil_Cap | Stage2SuppHVAC | Aux coil capacity
Notes_SuppHVAC | Stage2SuppHVAC | Includes any relevant information that may not be collected elsewhere
DOAS? | Stage2HRV | Does the system include a dedicated outdoor air system?
Equipment ID | Stage2HRV | Unique entry ID for each piece of HVAC equipment
Manufacturer | Stage2HRV | Manufacturer
Model | Stage2HRV | Model
OA Supply Airflow (CFM) | Stage2HRV | Outside Air Supply Airflow (CFM)
Exhaust Airflow (CFM) | Stage2HRV | Exhaust Airflow (CFM)
Fan Power | Stage2HRV | Fan Power
Fan Power Units | Stage2HRV | Fan Power Units
Sensible Effectiveness type | Stage2HRV | Indicates whether HRV/ERV sensible effectiveness was reported directly in drawings ("Direct") or calculated from entering/leaving air temperatures ("Calculated")
Sensible Effectiveness (%) | Stage2HRV | Sensible Effectiveness (%). -If included in project drawings, value is reported directly from drawings (noted as "direct" under sensible effectiveness type). -If not reported in drawings, sensible effectiveness is calculated from design airflows and temperatures (noted as "calculated" under sensible effectiveness type) using the following equation: Sensible Eff = [OA Airflow * (SA Temp - OA Temp)] / [Exhaust Airflow * (RA Temp - OA Temp)]
OA Temp (degree F) | Stage2HRV | Outdoor Air Temp (degree F) - Only populated if sensible effectiveness type is "calculated"
RA Temp (degree F) | Stage2HRV | Return Air Temp (degree F) - Only populated if sensible effectiveness type is "calculated"
SA Temp (degree F) | Stage2HRV | Supply Air Temp (degree F) - Only populated if sensible effectiveness type is "calculated"
Total Effectiveness (%) | Stage2HRV | Total Effectiveness (%), as reported in permit drawings
Supplemental heating type | Stage2HRV | Supplemental heating type
Supplemental heating fuel | Stage2HRV | Supplemental heating fuel

## Stage1ProjectData
Project_ID | Project_ID_code | Stage | Project_ID_mod | Site_City | Site_State | Site_Zip | Sq_ft | Completion_Date | Construction_Type | Council_Bldg_Type | Permit_Jurisdiction | Permit_Code_Cycle | Compliance_Path | Efficiency_Opt_1 | Efficiency_Opt_2 | Primary_Heating_System | Primay_Heat_Other | Primary_Cooling_System | Primary_Cool_Other | Primary_HeatFuel | Primary_HeatFuel_Other | SHS_VRF | SHS_DHP | SHS_PTHP | SHS_ASHP_Packaged | SHS_ASHP_Split | SCS_Ductless | SCS_PTAC | SCS_DXRTU | Ventilation_decoupled | HVAC_include_HRV | Sample_Weight
02- 705749-1 | 02- 705749-1 | Unconditioned or no new HVAC |  | Portland | OR | 97232 | 0 | 0 | New | Lodging | [21 empty] | 1
03- 779006-1 | 03- 779006-1 | Stage 2 |  | Woodburn | OR | 97071 | 5895 | 2018-09-01 | Alterations/Renovations, Interior Completions | School (K-12) | Woodburn, OR | 2014 OEESC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  | 1 | [7 empty] | Yes | Yes | 68
07- 670908-1 | 07- 670908-1 | Stage 1 |  | Seattle | WA | 98104 | 38297 | 2015-09-23 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas |  |  |  |  | 3 |  |  |  |  | No | No | 3.3333
07- 782313-1 | 07- 782313-1 | Stage 2 |  | Lakewood | WA | 98498 | 48190 | 2017-10-18 | New | Hospital | Lakewood, WA | 2015 IECC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | Yes | Yes | 4.6
07- 852054-1 | 07- 852054-1 | Project not completed |  | Seattle | WA | 98101 | 0 | 0 | New | Multi-Family Residential | [21 empty] | 1
07- 852054-3 | 07- 852054-3 | Project not completed |  | Seattle | WA | 98101 | 0 | 0 | New | Retail | [21 empty] | 2
07- 857252-1 | 07- 857252-1 | Stage 1 |  | Boise | ID | 83704 | 16000 | 2015-09-14 | New | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 1 |  |  | No | No | 9.5
07- 902856-1 | 07- 902856-1 | Stage 1 |  | Missoula | MT | 59812 | 145000 | 2017-09-01 | New | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | Yes | Yes | 4
08- 723130-1 | 08- 723130-1 | Stage 2 |  | SeaTac | WA | 98198 | 7500 | 2016-01-01 | New | Other | SeaTac, WA | 2015 SEC | Prescriptive |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | Yes | 20
08- 755856-1 | 08- 755856-1 | Stage 1 |  | Seattle | WA | 98104 | 19564 | 2016-05-09 | New | Lodging | [5 empty] | Air to Water Heat Pump |  | Water Cooled Chiller |  | Electric | [9 empty] | No | No | 1.4
08- 755856-2 | 08- 755856-2 | Stage 1 |  | Seattle | WA | 98104 | 485672 | 2016-05-09 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas |  |  | 11 | [6 empty] | No | No | 3.2
09- 503452-1 | 09- 503452-1 | Stage 1 |  | Seattle | WA | 98195 | 28771 | 2019-10-01 | New | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 2.5
09- 581175-1 | 09- 581175-1 | Stage 2 |  | Tukwila | WA | 98188 | 12540 | 2019-09-01 | New | Other | Tukwila, WA |  | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 1 | [6 empty] | Yes | Yes | 6.5
09- 603654-1 | 09- 603654-1 | Project not completed |  | Missoula | MT | 59802 | 0 | 0 | New | Assembly | [21 empty] | 2.75
09- 622054-1 | 09- 622054-1 | Unconditioned or no new HVAC |  | Portland | OR | 97225 | 0 | 0 | Alterations/Renovations, Additions | Hospital | [21 empty] | 1.2
09- 658527-1 | 09- 658527-1 | Stage 1 |  | Seattle | WA | 98122 | 347000 | 2020-03-03 | New | Other | [5 empty] | Boiler (Hot water or steam) |  | Air to Water Heat Pump |  | Natural Gas | [5 empty] | 3 |  |  |  | Yes | Yes | 1
10- 554480-1 | 10- 554480-1 | Stage 1 |  | Bremerton | WA | 98337 | 70000 | 2015-10-02 | New | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Other | No cooling system defined in project scope, existing cooling system | Natural Gas | [9 empty] | No | No | 2.2
10- 714727-1 | 10- 714727-1 | Stage 1 |  | Salem | OR | 97304 | 27800 | 2018-05-23 | Alterations/Renovations, Interior Completions | Residential Care | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas | [6 empty] | 3 |  |  | Yes | No | 5.6667
10- 718878-1 | 10- 718878-1 | Unconditioned or no new HVAC |  | Portland | OR | 97204 | 0 | 0 | Alterations/Renovations, Interior Completions | Office | [21 empty] | 3.3333
11- 468179-1 | 11- 468179-1 | Stage 2 |  | Portland | OR | 97230 | 2717 | 2020-05-29 | Alterations/Renovations, Additions | Assembly | Portland, OR | 2014 OEESC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 16.5
11- 531122-1 | 11- 531122-1 | Stage 2 |  | Portland | OR | 97204 | 1020 | 2017-08-28 | New | Other | Portland, OR |  |  |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 1
11- 556107-1 | 11- 556107-1 | Stage 2 |  | Lake Oswego | OR | 97305 | 8900 | 2019-07-12 | New | Assembly | Lake Oswego, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired indoor air handling unit |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 20.2
11- 631833-2 | 11- 631833-2 | Stage 2 |  | Tacoma | WA | 98407 | 143066 | 2019-12-01 | New | Residential Care | Tacoma, WA | 2015 WSEC | Prescriptive | More efficient HVAC | DOAS | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 7 |  |  | Yes | Yes | 5.6667
11- 656138-1 | 11- 656138-1 | Stage 2 |  | Bend | OR | 97701 | 80532 | 2018-03-26 | New | Lodging | Bend, OR |  |  |  |  | Other | Wall mounted electric heater | Direct Expansion Split System Air Handler |  | Electric | [9 empty] | Yes | Yes | 10
11- 661187-1 | 11- 661187-1 | Stage 1 |  | Portland | OR | 97210 | 28000 | 2015-08-05 | Alterations/Renovations, Interior Completions | Retail | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas | [6 empty] | 1 |  |  | Yes | No | 3.75
12- 456419-1 | 12- 456419-1 | Stage 2 |  | Boise | ID | 83706 | 347094 | 2015-01-29 | New | Multi-Family Residential | Boise, ID |  |  |  |  | Other | Central electric Forced Air Furnace | Direct Expansion Split System Air Handler |  | Electric | [6 empty] | 1 |  |  | No | No | 4
12- 473640-3 | 12- 473640-3 | Stage 1 |  | Seattle | WA | 98101 | 15000 | 2017-06-01 | New | Retail | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | No | No | 3.75
12- 508061-1 | 12- 508061-1 | Stage 1 |  | Seattle | WA | 98101 | 515000 | 2016-01-15 | New | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 2.5
12- 508061-2 | 12- 508061-2 | Stage 1 |  | Seattle | WA | 98101 | 235760 | 2016-01-15 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas |  | 4 | [6 empty] | 1 | No | Yes | 1
12- 585811-1 | 12- 585811-1 | Stage 1 |  | Nampa | ID | 83651 | 5500 | 2019-05-12 | New | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | No | No | 1
12- 637258-1 | 12- 637258-1 | Stage 1 |  | Seattle | WA | 98104 | 1500000 | 2020-01-01 | Additions | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas |  |  | 24 | [5 empty] | 3 | No | No | 1
12- 684272-1 | 12- 684272-1 | Stage 1 |  | Seattle | WA | 98109 | 139000 | 2017-11-03 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | No | No | 7.75
12- 701660-1 | 12- 701660-1 | Stage 2 |  | Portland | OR | 97232 | 54392 | 2015-07-15 | New | Office | Portland, OR | 2014 OEESC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | No | Yes | 26.3333
13- 401832-1 | 13- 401832-1 | Stage 1 |  | Whitefish | MT | 59937 | 10526 | 2017-05-22 | New | Other | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas | [6 empty] | 2 |  |  | No | No | 2.4
13- 404186-1 | 13- 404186-1 | Stage 2 |  | Everett | WA | 98208 | 7898 | 2018-05-04 | Alterations/Renovations, Additions | Other | Everett, WA | 2015 WSEC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | Yes | Yes | 2.3333
13- 427580-1 | 13- 427580-1 | Stage 1 |  | Bellevue | WA | 98004 | 357000 | 2017-10-18 | New | Office | [5 empty] | Zonal Electric |  | Air Cooled Chiller |  | Electric |  |  |  | 1 | [5 empty] | No | No | 7.2
13- 433118-1 | 13- 433118-1 | Stage 1 |  | Corvallis | OR | 97333 | 58000 | 2016-01-01 | New | School (University) | [5 empty] | Other | District steam heating system | Other | District chilled water system | Natural Gas | [9 empty] | Yes | Yes | 2.2
13- 454968-1 | 13- 454968-1 | Stage 1 |  | Seattle | WA | 98104 | 303866 | 2020-05-07 | New | Multi-Family Residential | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas |  |  | 3 |  |  | 1 |  |  | 1 | Yes | No | 13
13- 492091-1 | 13- 492091-1 | Stage 1 |  | Kettle Falls | WA | 99141 | 3113 | 2016-03-07 | Alterations/Renovations, Additions | Assembly | [5 empty] | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas | [6 empty] | 2 |  |  | No | No | 32.75
13- 523894-1 | 13- 523894-1 | Stage 1 |  | Pullman | WA | 99163 | 68959 | 2016-03-22 | Alterations/Renovations, Interior Completions | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | No | Yes | 3.75
13- 532988-1 | 13- 532988-1 | Stage 1 |  | Portland | OR | 97203 | 231941 | 2015-12-10 | Alterations/Renovations, Interior Completions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [8 empty] | 2 | Yes | Yes | 8.5
13- 541287-1 | 13- 541287-1 | Unconditioned or no new HVAC |  | Butte | MT | 59701 | 0 | 0 | Alterations/Renovations, Additions | School (University) | [21 empty] | 6
13- 586583-1 | 13- 586583-1 | Stage 1 |  | Portland | OR | 97201 | 202344 | 2016-01-21 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [9 empty] | Yes | No | 2.75
13- 597289-1 | 13- 597289-1 | Stage 1 |  | Cheney | WA | 99004 | 168795 | 2019-01-01 | Alterations/Renovations, Interior Completions | Assembly | [5 empty] | Zonal Electric |  | Water Cooled Chiller |  | Electric | [6 empty] | 6 |  |  | No | Yes | 2.75
13- 636582-1 | 13- 636582-1 | Stage 2 |  | Liberty Lake | WA | 99019 | 81330 | 2015-06-01 | New | Office | Liberty Lake, WA | 2012 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 3 | [6 empty] | No | No | 2.625
13- 658146-1 [Natatorium] | 13- 658146-1 | Stage 2 | Natatorium | Bend | OR | 97702 | 9717 | 2018-10-26 | Alterations/Renovations, Additions | Assembly | Bend , OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 1.0717
13- 658146-1 [Other] | 13- 658146-1 | Stage 2 | Other | Bend | OR | 97702 | 24283 | 2018-10-26 | Alterations/Renovations, Additions | Assembly | Bend, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 2.6783
13- 682869-1 | 13- 682869-1 | Unconditioned or no new HVAC |  | Portland | OR | 97239 | 0 | 0 | New | Office | [21 empty] | 3.3333
13- 684174-1 [Chiller] | 13- 684174-1 | Stage 1 | Chiller | Seattle | WA | 98109 | 575530 | 2019-01-04 | New | Multi-Family Residential | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas |  |  | 7 | [6 empty] | No | Yes | 0.51154
13- 684174-1 [Cooling tower] | 13- 684174-1 | Stage 1 | Cooling tower | Seattle | WA | 98109 | 549554 | 2019-01-04 | New | Multi-Family Residential | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas |  |  | 7 | [6 empty] | No | Yes | 0.48846
13- 702104-1 | 13- 702104-1 | Stage 1 |  | Caldwell | ID | 83605 | 8792 | 2014-11-17 | Additions | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [6 empty] | 1 |  |  | No | No | 5.6667
14- 407263-2 | 14- 407263-2 | Stage 1 |  | Beaverton | OR | 97229 | 131050 | 2016-07-13 | New, Add, Alt or New, Add, Interior Completions | Residential Care | [5 empty] | Gas-fired indoor air handling unit |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 10
14- 426751-1 | 14- 426751-1 | Stage 2 |  | Kennewick | WA | 99336 | 12556 | 2015-07-28 | New | Other | Kennewick, WA | 2012 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  | 3 | [7 empty] | No | Yes | 9.6667
14- 445547-1 | 14- 445547-1 | Stage 1 |  | Pullman | WA | 99164 | 95000 | 2020-11-16 | New | School (University) | [5 empty] | Gas-fired indoor air handling unit |  | Water Cooled Chiller |  | Natural Gas |  |  |  |  | 3 |  |  |  |  | Yes | No | 1
14- 461716-2 | 14- 461716-2 | Stage 1 |  | Seattle | WA | 98101 | 307296 | 2016-02-01 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas |  |  | 1 |  | 1 |  |  |  |  | Yes | No | 7.2
14- 486801-1 | 14- 486801-1 | Stage 1 |  | Pullman | WA | 99164 | 83000 | 2017-12-01 | New | School (University) | [5 empty] | Gas-fired indoor air handling unit |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 5
14- 493663-2 | 14- 493663-2 | Stage 2 |  | Portland | OR | 97209 | 367000 | 2016-03-21 | New | Office | Portland, OR | 2014 OEESC | Total Building Performance |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 26.3333
14- 494370-1 | 14- 494370-1 | Stage 1 |  | Tacoma | WA | 98402 | 285000 | 2017-06-01 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas |  | 2 |  |  |  |  | 3 |  | 1 | Yes | Yes | 2.75
14- 494803-1 | 14- 494803-1 | Stage 2 |  | Pasco | WA | 99301 | 38000 | 2017-02-27 | New | Other | Pasco, WA | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 3 | [6 empty] | Yes | Yes | 6
14- 522417-3 | 14- 522417-3 | Stage 1 |  | Seattle | WA | 98101 | 722000 | 2018-11-13 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [9 empty] | Yes | Yes | 1
14- 522417-5 | 14- 522417-5 | Stage 1 |  | Seattle | WA | 98101 | 722000 | 2019-05-21 | New | Retail | [5 empty] | Other | Heat Pump Chiller | Water Cooled Chiller | Heat Pump Chiller | Electric | [5 empty] | 1 |  |  |  | Yes | No | 2
14- 523662-1 | 14- 523662-1 | Stage 1 |  | Bellevue | WA | 98004 | 4127 | 2017-08-03 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 2 | 2 |  |  | Yes | Yes | 21.6667
14- 526453-1 [DHP] | 14- 526453-1 | Stage 2 | DHP | Seattle | WA | 98109 | 151810 | 2017-10-08 | New | Multi-Family Residential | Seattle, WA | 2012 SEC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [6 empty] | 3 |  |  | No | No | 15.8173
14- 526453-1 [RTU] | 14- 526453-1 | Stage 2 | RTU | Seattle | WA | 98109 | 184110 | 2017-10-08 | New | Multi-Family Residential | Seattle, WA | 2012 SEC | Prescriptive |  |  | Packaged Terminal Heat Pump |  | Packaged Terminal Heat Pump |  | Electric | [9 empty] | No | No | 19.1827
14- 533540-1 | 14- 533540-1 | Stage 1 |  | Seattle | WA | 98121 | 505173 | 2016-02-07 | New | Multi-Family Residential | [5 empty] | Gas-fired indoor air handling unit |  | Air Cooled Chiller |  | Natural Gas | [9 empty] | No | No | 4.6667
14- 534266-1 | 14- 534266-1 | Unconditioned or no new HVAC |  | Bend | OR | 97701 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 2.3333
14- 539253-1 | 14- 539253-1 | Unconditioned or no new HVAC |  | Richland | WA | 99352 | 0 | 0 | Additions | Hospital | [21 empty] | 2.6667
14- 540112-1 [Corridors\Main Floor Areas] | 14- 540112-1 | Stage 2 | Corridors\Main Floor Areas | Seattle | WA | 98103 | 19488 | 2015-11-25 | New | Multi-Family Residential | Seattle, WA | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 1 |  |  |  | Yes | No | 47.879
14- 540112-1 [Misc.] | 14- 540112-1 | Stage 2 | Misc. | Seattle | WA | 98103 | 17280 | 2015-11-25 | New | Multi-Family Residential | Seattle, WA | 2012 IECC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | Yes | No | 42.4543
14- 544262-1 | 14- 544262-1 | Stage 1 |  | Pendleton | OR | 97801 | 15722 | 2018-06-15 | New | Other | [5 empty] | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas | [5 empty] | 1 | 15 |  |  | Yes | Yes | 2.4
14- 550027-2 | 14- 550027-2 | Stage 2 |  | Eugene | OR | 97401 | 159606 | 2017-08-30 | New | Residential Care | Eugene, OR | 2014 OEESC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  |  | 3 |  |  | 1 |  |  | Yes | Yes | 1.6
14- 577214-1 | 14- 577214-1 | Stage 1 |  | Seattle | WA | 98104 | 45000 | 2016-01-01 | New | Restaurant | [5 empty] | Gas-fired indoor air handling unit |  | Air Cooled Chiller |  | Natural Gas | [5 empty] | 1 |  | 1 |  | Yes | Yes | 6.5
14- 579875-1 | 14- 579875-1 | Stage 2 |  | Clarkston | WA | 99403 | 2594 | 2018-01-01 | Alterations/Renovations, Additions | Assembly | Clarkston, WA | 2015 IECC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 32.75
14- 581893-1 | 14- 581893-1 | Unconditioned or no new HVAC |  | Renton | WA | 98057 | 0 | 0 | New | Retail | [21 empty] | 2
14- 585301-1 | 14- 585301-1 | Stage 1 |  | Lynnwood | WA | 98036 | 68000 | 2016-02-02 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air to Water Heat Pump |  | Natural Gas | [8 empty] | 6 | No | Yes | 49
14- 587282-1 | 14- 587282-1 | Stage 2 |  | Auburn | WA | 98047 | 228270 | 2016-04-01 | New | Residential Care | Auburn, WA | 2012 WSEC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 2 |  |  | No | Yes | 10
14- 595997-1 | 14- 595997-1 | Stage 1 |  | Corvallis | OR | 97331 | 97400 | 2017-01-01 | Alterations/Renovations, Interior Completions | School (University) | [5 empty] | Other | District steam heating system | Variable Refrigerant Flow |  | Natural Gas | [9 empty] | Yes | No | 40
14- 611061-1 | 14- 611061-1 | Stage 2 |  | Seattle | WA | 98115 | 2690 | 2016-01-19 | New | Multi-Family Residential | Seattle, WA | 2012 WSEC |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric |  |  | 1 | [6 empty] | Yes | No | 143
14- 612212-1 | 14- 612212-1 | Stage 1 |  | Seattle | WA | 98109 | 13847 | 2016-08-05 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas | [9 empty] | No | No | 7.75
14- 626014-1 | 14- 626014-1 | Stage 2 |  | Newcastle | WA | 98056 | 128512 | 2018-01-01 | New | Residential Care | Newcastle, WA | 2012 WSEC | Total Building Performance |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric |  |  |  | 4 |  |  | 3 |  |  | Yes | Yes | 1.6
14- 634379-1 | 14- 634379-1 | Stage 2 |  | Walla Walla | WA | 99362 | 208217 | 2018-07-02 | New, Alterations or New, Interior Completions | Retail | Walla Walla, WA | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [11 empty] | 1
14- 662676-1 | 14- 662676-1 | Stage 2 |  | Seattle | WA | 98126 | 16366 | 2017-02-01 | Alterations/Renovations, Additions | Assembly | Seattle, WA | 2012 SEC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 1 |  |  |  | No | No | 20.2
14- 668269-1 | 14- 668269-1 | Stage 2 |  | Renton | WA | 98056 | 730343 | 2018-12-01 | New | Office | Renton, WA | 2012 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 1
14- 673478-1 | 14- 673478-1 | Stage 1 |  | Springfield | OR | 97477 | 157000 | 2019-05-01 | New, Alterations or New, Interior Completions | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas |  |  | 14 |  |  |  | 2 |  | 3 | Yes | Yes | 1.2
14- 673795-2 | 14- 673795-2 | Stage 2 |  | Portland | OR | 97210 | 51713 | 2016-08-02 | New | Retail | Portland, OR | 2014 OEESC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 3.75
14- 674569-1 | 14- 674569-1 | Stage 1 |  | Eugene | OR | 97401 | 246520 | 2019-08-01 | New | Lodging | [5 empty] | Packaged Terminal Heat Pump |  | Packaged Terminal Heat Pump |  | Electric |  | 3 |  |  | 2 |  | 2 |  | 1 | Yes | Yes | 21.6667
14- 689118-1 | 14- 689118-1 | Stage 2 |  | Portland | OR | 97201 | 135942 | 2018-04-14 | New | Multi-Family Residential | Portland, OR |  | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 3 | 4 |  | 23 | 2 |  |  | Yes | Yes | 13
14- 711862-1 | 14- 711862-1 | Stage 1 |  | Seattle | WA | 98101 | 207000 | 2018-01-01 | New | School (University) | [5 empty] | Other | Unit heaters | Direct Expansion Split System Air Handler |  | Natural Gas |  |  | 1 | [6 empty] | Yes | Yes | 1.6667
14- 718467-1 | 14- 718467-1 | Unconditioned or no new HVAC |  | Portland | OR | 97232 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 2.75
14- 720685-1 | 14- 720685-1 | Stage 1 |  | Seattle | WA | 98125 | 258890 | 2015-02-09 | Alterations/Renovations, Interior Completions | School (K-12) | [5 empty] | Other | Existing steam boiler | Other | Existing chiller | Natural Gas |  |  | 1 | [6 empty] | No | No | 108.6667
14- 722894-2 | 14- 722894-2 | Stage 1 |  | Eugene | OR | 97440 | 166000 | 2020-01-01 | New | School (University) | [5 empty] | Other | District Steam Heating System | Water Cooled Chiller | Heat Recovery Chiller | Natural Gas | [6 empty] | 2 |  |  | Yes | Yes | 1.6667
14- 725982-1 | 14- 725982-1 | Unconditioned or no new HVAC |  | Tacoma | WA | 98405 | 0 | 0 | New | Hospital | [21 empty] | 1.2
14- 730160-1 | 14- 730160-1 | Stage 2 |  | Spokane | WA | 99206 | 51260 | 2016-03-18 | New | Other | Spokane, WA |  |  |  |  | Zonal Electric |  | Ductless Heat Pump |  | Electric |  | 50 | [7 empty] | No | Yes | 2.4
14- 731874-1 [RTU] | 14- 731874-1 | Stage 2 | RTU | Clarkston | WA | 99403 | 13000 | 2016-03-07 | New | School (University) | Clarkston, WA | 2012 WSEC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 10.5072
14- 731874-1 [VRF] | 14- 731874-1 | Stage 2 | VRF | Clarkston | WA | 99403 | 4940 | 2016-03-07 | New | School (University) | Clarkston, WA | 2012 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Cooling Tower |  | Electric |  |  | 2 |  |  |  | 1 |  |  | No | Yes | 3.9928
15- 400358-1 | 15- 400358-1 | Stage 1 |  | Ketchum | ID | 83340 | 175000 | 2015-05-20 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 2
15- 411019-1 | 15- 411019-1 | Stage 1 |  | Pullman | WA | 99164 | 19095 | 2016-06-16 | New, Alterations or New, Interior Completions | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Other | District chilled water system | Natural Gas | [9 empty] | No | No | 6
15- 411092-1 | 15- 411092-1 | Stage 2 |  | Rexburg | ID | 83440 | 160000 | 2016-01-27 | New | Retail | Rexburg, ID |  | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 4.6667
15- 412479-1 | 15- 412479-1 | Stage 1 |  | Missoula | MT | 59802 | 97170 | 2018-09-18 | New | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | No | Yes | 2.75
15- 419195-1 | 15- 419195-1 | Unconditioned or no new HVAC |  | Pendleton | OR | 97801 | 0 | 0 | New | School (K-12) | [21 empty] | 29
15- 419203-1 [Additional Areas] | 15- 419203-1 | Stage 2 | Additional Areas | Pendleton | OR | 97801 | 37141 | 2016-08-01 | New | School (K-12) | Pendleton, OR | 2014 OEESC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | No | No | 16.8198
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | 15- 419203-1 | Stage 2 | Gym, Cafeteria, North Wing, South Wing | Pendleton | OR | 97801 | 26896 | 2016-08-01 | New | School (K-12) | Pendleton, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | Yes | Yes | 12.1802
15- 419460-1 | 15- 419460-1 | Stage 2 |  | Forest Grove | OR | 97116 | 7530 | 2018-06-05 | Alterations/Renovations, Interior Completions | Residential Care | Forest Grove, OR | 2014 OEESC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 1 | [6 empty] | Yes | Yes | 1.6
15- 425673-1 | 15- 425673-1 | Stage 2 |  | Vancouver | WA | 98661 | 13367 | 2018-06-28 | New | Other | Vancouver, WA | 2012 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 6.5
15- 427602-1 | 15- 427602-1 | Stage 2 |  | Everett | WA | 98203 | 60167 | 2019-12-01 | New | Assembly | Everett, WA | 2015 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 2 |  |  | No | No | 7
15- 440965-1 | 15- 440965-1 | Stage 1 |  | Seattle | WA | 98109 | 650000 | 2017-05-19 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas |  |  | 2 |  |  | 4 |  |  |  | No | No | 3.2
15- 457921-1 | 15- 457921-1 | Unconditioned or no new HVAC |  | Portland | OR | 97222 | 0 | 0 | New | School (University) | [21 empty] | 10.6
15- 458201-1 | 15- 458201-1 | Stage 2 |  | Boise | ID | 83702 | 100240 | 2017-10-01 | New | Lodging | Boise, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 2 | 3 |  |  | 3 |  |  | Yes | No | 2
15- 464466-1 | 15- 464466-1 | Stage 2 |  | Boise | ID | 83702 | 90000 | 2015-11-20 | New | Lodging | Boise, ID | 2012 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [8 empty] | 2 | Yes | Yes | 2
15- 472302-1 | 15- 472302-1 | Stage 1 |  | Newport | OR | 97365 | 126000 | 2020-07-01 | New | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [9 empty] | Yes | No | 1.2
15- 483817-1 | 15- 483817-1 | Stage 1 |  | Spokane | WA | 99206 | 63519 | 2017-08-29 | Alterations/Renovations, Additions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 5 |  |  | Yes | Yes | 19
15- 483988-1 | 15- 483988-1 | Unconditioned or no new HVAC |  | Woodland | WA | 98674 | 0 | 0 | New | Restaurant | [21 empty] | 16
15- 506066-2 | 15- 506066-2 | Stage 1 |  | Seattle | WA | 98101 | 500000 | 2016-01-01 | New | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Other | Air-Cooled Heat Recovery Chiller | Natural Gas | [9 empty] | Yes | Yes | 1
15- 527020-1 | 15- 527020-1 | Stage 2 |  | Boise | ID | 83702 | 4992 | 2016-01-01 | Alterations/Renovations, Interior Completions | Restaurant | Boise, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 2.25
15- 539739-1 | 15- 539739-1 | Stage 1 |  | Salem | OR | 97301 | 12797 | 2020-10-10 | New | Other | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 5 |  |  | Yes | Yes | 2.3333
15- 568036-2 | 15- 568036-2 | Stage 2 |  | Portland | OR | 97266 | 29000 | 2017-01-04 | New | Retail | Portland, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 4 |  |  | 3 | 2 |  |  | No | No | 31.5
15- 568461-1 | 15- 568461-1 | Project not completed |  | Corvallis | OR | 97333 | 0 | 0 | Alterations/Renovations, Interior Completions | School (University) | [21 empty] | 2.2
15- 573278-1 | 15- 573278-1 | Stage 2 |  | Missoula | MT | 59801 | 48940 | 2017-06-01 | Alterations/Renovations, Additions | Retail | Missoula, MT | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 5 |  |  | No | No | 1
15- 577343-2 | 15- 577343-2 | Stage 1 |  | Snoqualmie | WA | 98065 | 366862 | 2019-09-01 | New, Add, Alt or New, Add, Interior Completions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [5 empty] | 2 | 11 |  |  | Yes | Yes | 1
15- 577408-1 | 15- 577408-1 | Unconditioned or no new HVAC |  | Snoqualmie | WA | 98065 | 0 | 0 | Alterations/Renovations, Interior Completions | School (K-12) | [21 empty] | 108.6667
15- 580950-1 | 15- 580950-1 | Stage 2 |  | Seattle | WA | 98121 | 586921 | 2016-04-19 | New | Multi-Family Residential | Seattle, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | No | 4.6667
15- 581819-1 | 15- 581819-1 | Unconditioned or no new HVAC |  | Lynnwood | WA | 98087 | 0 | 0 | Alterations/Renovations, Additions | Residential Care | [21 empty] | 1.6
15- 589031-1 | 15- 589031-1 | Stage 2 |  | Meridian | ID | 83642 | 2218 | 2016-05-19 | New | Assembly | Meridian, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 21.3333
15- 590241-1 | 15- 590241-1 | Stage 1 |  | Pullman | WA | 99164 | 63265 | 2021-01-01 | New | School (University) | [5 empty] | Other | Connected to the District heating and cooling system at the WSU campus | Other | Connected to the District heating and cooling system at the WSU campus | Natural Gas | [9 empty] | No | Yes | 1
15- 594519-1 | 15- 594519-1 | Stage 1 |  | Cheney | WA | 99004 | 101352 | 2017-07-07 | New | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [6 empty] | 2 |  |  | Yes | Yes | 5
15- 602446-1 | 15- 602446-1 | Stage 2 |  | Gooding | ID | 83330 | 100000 | 2015-11-19 | New | Office | Gooding, ID | 2012 IECC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 48
15- 610152-1 | 15- 610152-1 | Unconditioned or no new HVAC |  | Kirkland | WA | 98033 | 0 | 0 | New | Office | [21 empty] | 3.2
15- 617169-1 | 15- 617169-1 | Stage 1 |  | Myrtle Creek | OR | 97457 | 9100 | 2015-08-18 | New | Retail | [5 empty] | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 119
15- 630595-1 | 15- 630595-1 | Stage 1 |  | Portland | OR | 97204 | 231087 | 2017-12-13 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [6 empty] | 5 |  |  | Yes | No | 7.2
15- 635115-1 | 15- 635115-1 | Project not completed |  | Coeur D Alene | ID | 83814 | 0 | 0 | New | Restaurant | [21 empty] | 8
15- 640275-1 [Common Areas and Corridors] | 15- 640275-1 | Stage 2 | Common Areas and Corridors | Kalispell | MT | 59901 | 9614.4 | 2017-08-01 | Alterations/Renovations, Additions | Residential Care | Kalispell, MT |  |  |  |  | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | yes | yes | 2.25
15- 640275-1 [Residences] | 15- 640275-1 | Stage 2 | Residences | Kalispell | MT | 59901 | 6409.6 | 2017-08-01 | Alterations/Renovations, Additions | Residential Care | Kalispell, MT | 2012 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | yes | yes | 1.5
15- 668067-1 | 15- 668067-1 | Unconditioned or no new HVAC |  | The Dalles | OR | 97058 | 0 | 0 | New | Office | [21 empty] | 2.625
15- 669524-1 | 15- 669524-1 | Stage 1 |  | Seattle | WA | 98109 | 104246 | 2016-01-01 | New | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Other | Active Chilled Beam | Natural Gas | [9 empty] | Yes | Yes | 1.6667
15- 670579-1 | 15- 670579-1 | Stage 1 |  | Seattle | WA | 98117 | 29000 | 2019-10-12 | New | Assembly | [5 empty] | Air to Water Heat Pump |  | Air to Water Heat Pump |  | Electric | [9 empty] | No | Yes | 7
15- 674826-1 | 15- 674826-1 | Stage 1 |  | Seattle | WA | 98101 | 329054 | 2017-01-18 | New | Multi-Family Residential | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas |  |  | 5 | [6 empty] | Yes | Yes | 4.6667
15- 689971-1 | 15- 689971-1 | Stage 2 |  | Boise | ID | 83716 | 15266 | 2016-04-01 | New | Multi-Family Residential | Boise, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 4 |  |  | No | No | 4
15- 690453-1 | 15- 690453-1 | Unconditioned or no new HVAC |  | Kennewick | WA | 99336 | 0 | 0 | New | Retail | [21 empty] | 18
15- 692220-1 | 15- 692220-1 | Stage 2 |  | Portland | OR | 97209 | 7328 | 2017-07-24 | New | Multi-Family Residential | Portland, OR | 2014 OEESC |  |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 55
15- 700290-1 | 15- 700290-1 | Stage 2 |  | Coeur D Alene | ID | 83816 | 6276 | 2016-06-01 | Alterations/Renovations, Interior Completions | Restaurant | Coeur D Alene, ID |  | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 8
16- 400924-1 | 16- 400924-1 | Stage 2 |  | Lacey | WA | 98503 | 78000 | 2019-07-16 | Alterations/Renovations, Interior Completions | Hospital | Lacey, WA |  |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 10 |  |  |  | Yes | No | 4.6
16- 403736-1 | 16- 403736-1 | Stage 2 |  | Portland | OR | 97227 | 330000 | 2020-01-01 | Alterations/Renovations, Additions | Hospital | Portland, OR |  |  |  |  | Other | District steam heating system | Air Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 1.5
16- 404663-1 | 16- 404663-1 | Stage 2 |  | Bellevue | WA | 98004 | 95034 | 2020-05-18 | New | Residential Care | Bellevue, WA | 2015 WSEC | Prescriptive | DOAS |  | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas |  |  | 1 |  |  |  | 2 | 1 |  | Yes | No | 1
16- 406071-1 | 16- 406071-1 | Stage 1 |  | Bend | OR | 97709 | 25400 | 2016-06-27 | New | Multi-Family Residential | [5 empty] | Packaged Terminal Heat Pump |  | Packaged Terminal Heat Pump |  | Electric | [9 empty] | No | No | 34
16- 407620-1 | 16- 407620-1 | Stage 1 |  | Eugene | OR | 97403 | 160800 | 2019-10-01 | Alterations/Renovations, Additions | Lodging | City of Eugene |  | Prescriptive |  |  | Other | District steam heating system | Other | District chilled water | Natural Gas | [6 empty] | 1 |  |  | No | Yes | 7.75
16- 412293-1 | 16- 412293-1 | Stage 2 |  | Medford | OR | 97501 | 90000 | 2016-10-07 | New | Retail | Medford, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 19
16- 418625-1 | 16- 418625-1 | Project not completed |  | Seattle | WA | 98105 | 0 | 0 | New, Alterations or New, Interior Completions | Lodging | [21 empty] | 1.4
16- 423218-1 | 16- 423218-1 | Stage 2 |  | Boise | ID | 83706 | 151000 | 2017-03-20 | New | Multi-Family Residential | Boise, ID | 2012 IECC | Prescriptive |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric |  |  | 2 |  |  |  | 1 |  |  | No | No | 9.6667
16- 427879-1 | 16- 427879-1 | Stage 2 |  | Kennewick | WA | 99336 | 19991 | 2021-08-05 | Alterations/Renovations, Interior Completions | Hospital | Kennewick, WA | 2012 WSEC | Total Building Performance |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | No | No | 5.6667
16- 429395-1 | 16- 429395-1 | Stage 2 |  | Shoreline | WA | 98155 | 60625 | 2017-08-19 | Alterations/Renovations, Additions | Residential Care | Shoreline, WA | 2012 WSEC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  |  | 1 |  |  | 1 |  |  | No | No | 12.3333
16- 435265-1 | 16- 435265-1 | Stage 1 |  | Portland | OR | 97201 | 217000 | 2018-04-17 | Alterations/Renovations, Interior Completions | School (University) | [5 empty] | Other | District steam heating system | Other | District chilled water system | Natural Gas | [9 empty] | Yes | Yes | 2.2
16- 438381-1 | 16- 438381-1 | Stage 2 |  | Port Orchard | WA | 98366 | 22000 | 2017-07-24 | New, Alterations or New, Interior Completions | Retail | Port Orchard, WA | 2012 WSEC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 88
16- 442030-1 | 16- 442030-1 | Stage 2 |  | Seattle | WA | 98109 | 132291 | 2018-05-25 | New | Multi-Family Residential | Seattle, WA |  |  |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric |  | 1 | [6 empty] | 2 | Yes | Yes | 143
16- 445036-1 | 16- 445036-1 | Unconditioned or no new HVAC |  | Bellevue | WA | 98007 | 0 | 0 | Alterations/Renovations, Interior Completions | Assembly | [21 empty] | 20.2
16- 448078-1 | 16- 448078-1 | Project not completed |  | Spokane | WA | 99210 | 0 | 0 | New | Restaurant | [21 empty] | 2.25
16- 451264-1 | 16- 451264-1 | Unconditioned or no new HVAC |  | Bellevue | WA | 98004 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 4.6
16- 486864-4 | 16- 486864-4 | Unconditioned or no new HVAC |  | Beaverton | OR | 97076 | 0 | 0 | New | Retail | [21 empty] | 2
16- 490400-1 | 16- 490400-1 | Stage 2 |  | West Richland | WA | 99353 | 13990 | 2019-02-28 | New | Other | West Richland, WA | 2015 WSEC | Prescriptive | Enhanced envelope performance |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 1 |  |  |  | 1 |  |  | No | Yes | 9.6667
16- 493021-1 | 16- 493021-1 | Stage 1 |  | Lincoln City | OR | 97367 | 18941 | 2015-09-01 | Alterations/Renovations, Additions | Hospital | [5 empty] | Other | Existing VAV system with hot water reheat | Other | Existing VAV system (DX assumed) | Natural Gas | [6 empty] | 1 |  | 1 | No | No | 2.75
16- 495857-1 | 16- 495857-1 | Stage 2 |  | Silverdale | WA | 98383 | 54178 | 2017-04-27 | New | Hospital | Silverdale, WA | 2015 IECC | Prescriptive |  |  | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [5 empty] | 1 | 2 |  |  | No | Yes | 1.5
16- 501238-1 | 16- 501238-1 | Stage 1 |  | Renton | WA | 98057 | 18650 | 2020-02-01 | Alterations/Renovations, Interior Completions | School (University) | City of Renton | 2015 SEC | Prescriptive |  |  | Zonal Electric | VAV with electric reheat | Other | Existing unknown VAV Cooling (likely DX) | Electric | [9 empty] | Yes | Yes | 10.6
16- 505459-1 | 16- 505459-1 | Stage 2 |  | Nyssa | OR | 97913 | 52003 | 2018-08-01 | New | School (K-12) | Nyssa, OR | 2015 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 4 | [6 empty] | yes | yes | 33
16- 507255-1 [Corridors] | 16- 507255-1 | Stage 2 | Corridors | Spokane | WA | 99201 | 5311 | 2016-07-13 | New | Multi-Family Residential | Spokane, WA | 2015 WSEC | Prescriptive | More efficient HVAC | Additional Efficiency Options | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 3 |  |  | 3 | 3 |  |  | No | No | 4.8333
16- 507255-1 [Furnace] | 16- 507255-1 | Stage 2 | Furnace | Spokane | WA | 99201 | 5311 | 2016-07-13 | New | Multi-Family Residential | Spokane, WA |  |  |  |  | Gas-fired indoor air handling unit |  | None |  | Natural Gas | [9 empty] | No | No | 4.8333
16- 514976-1 | 16- 514976-1 | Stage 2 |  | Portland | OR | 97232 | 18321 | 2017-12-22 | New | Multi-Family Residential | Portland, OR | 2014 OEESC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 1 | 1 | [5 empty] | Yes | No | 35
16- 525524-1 | 16- 525524-1 | Stage 1 |  | Edgewood | WA | 98371 | 81372 | 2017-08-04 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 2 |  |  | No | No | 49
16- 534677-1 | 16- 534677-1 | Stage 1 |  | Eugene | OR | 97403 | 9150 | 2016-07-15 | Alterations/Renovations, Interior Completions | School (University) | [5 empty] | Other | Existing gas fired boiler (assumed – insufficient drawing information) | Other | Air cooled chiller (assumed – insufficient drawing information) | Natural Gas | [9 empty] | Yes | Yes | 40
16- 536718-1 | 16- 536718-1 | Stage 2 |  | Newport | WA | 99156 | 46772 | 2019-01-01 | New | Residential Care | Newport, WA | 2015 WSEC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  | 50 |  | 1 |  |  | 1 |  |  | No | Yes | 3.75
16- 537171-1 | 16- 537171-1 | Stage 2 |  | Portland | OR | 97230 | 107472 | 2017-11-14 | New | Office | Portland, OR | 2014 OEESC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 4 | [6 empty] | Yes | Yes | 7.2
16- 540071-1 | 16- 540071-1 | Stage 1 |  | Redmond | WA | 98052 | 77782 | 2016-09-09 | New | School (K-12) | [5 empty] | Ground Source / Ground Coupled Heat Pump |  | Ground Source / Ground Coupled Heat Pump |  | Electric | [9 empty] | Yes | No | 24.3333
16- 558605-2 | 16- 558605-2 | Stage 2 |  | Kirkland | WA | 98034 | 4086 | 2020-06-22 | New | Retail | Kirkland, WA | 2015 WSEC | Total Building Performance |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | Yes | Yes | 3.75
16- 570248-1 | 16- 570248-1 | Project not completed |  | Grand Coulee | WA | 99133 | 0 | 0 | New | Other | [21 empty] | 2.4
16- 572659-1 | 16- 572659-1 | Stage 2 |  | Meridian | ID | 83680 | 5250 | 2016-04-21 | Alterations/Renovations, Additions | Residential Care | Meridian, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [7 empty] | 2 |  | No | No | 7
16- 577162-1 | 16- 577162-1 | Stage 2 |  | Meridian | ID | 83680 | 6340 | 2016-04-14 | New | Hospital | Meridian, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 1 |  |  | No | No | 5.6667
16- 579846-1 | 16- 579846-1 | Stage 1 |  | Salem | OR | 97317 | 38400 | 2016-02-19 | Alterations/Renovations, Interior Completions | Office | [5 empty] | Packaged Terminal Heat Pump |  | Packaged Terminal Heat Pump |  | Electric | [9 empty] | No | No | 61
16- 600065-1 | 16- 600065-1 | Stage 1 |  | Meridian | ID | 83680 | 52500 | 2018-02-14 | New | Restaurant | [5 empty] | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas | [5 empty] | 1 |  |  |  | No | No | 2.25
16- 607207-1 | 16- 607207-1 | Stage 2 |  | Boise | ID | 83799 | 5925 | 2019-08-12 | New | Retail | Boise, ID | 2015 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 1 | [6 empty] | No | No | 20.6
16- 615057-1 | 16- 615057-1 | Stage 2 |  | Seattle | WA | 98119 | 9918 | 2017-01-24 | Alterations/Renovations, Additions | Residential Care | Seattle, WA | 2012 WSEC |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | No | 1
16- 615127-1 | 16- 615127-1 | Stage 2 |  | Burien | WA | 98166 | 23000 | 2016-06-29 | New | Office | Burien, WA |  |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 61
16- 619705-1 | 16- 619705-1 | Stage 1 |  | Lynnwood | WA | 98020 | 70000 | 2020-09-28 | Alterations/Renovations, Additions | School (University) | [5 empty] | Other | District steam heating system | Other | District chilled water system | Natural Gas | [5 empty] | 5 |  |  |  | No | Yes | 7.25
16- 621440-1 | 16- 621440-1 | Stage 2 |  | Vancouver | WA | 98687 | 2488 | 2019-04-01 | New | Restaurant | Vancouver, WA | 2015 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 16
16- 631283-1 | 16- 631283-1 | Stage 1 |  | Seattle | WA | 98199 | 41419 | 2016-07-10 | Alterations/Renovations, Interior Completions | School (University) | [5 empty] | Other | District Steam Heating | Other | Central Chilled Water Plant | Natural Gas | [9 empty] | No | No | 10.6
16- 631594-1 | 16- 631594-1 | Stage 1 |  | Seattle | WA | 98199 | 11826 | 2016-05-09 | Alterations/Renovations, Additions | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Other | Existing Chilled Water | Natural Gas | [9 empty] | Yes | Yes | 9.6
16- 640402-1 | 16- 640402-1 | Stage 2 |  | Seattle | WA | 98109 | 38880 | 2019-01-01 | New | Multi-Family Residential | Seattle, WA | 2015 SEC | Prescriptive | More efficient HVAC | DOAS | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | Yes | Yes | 143
16- 640577-1 | 16- 640577-1 | Stage 2 |  | Roseburg | OR | 97470 | 5628 | 2018-04-01 | New | Lodging | Roseburg, OR |  |  |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric |  |  |  | 2 | [5 empty] | Yes | No | 21.6667
16- 644391-1 | 16- 644391-1 | Unconditioned or no new HVAC |  | Bellingham | WA | 98225 | 0 | 0 | Alterations/Renovations, Additions | School (University) | [21 empty] | 10.6
16- 646137-1 | 16- 646137-1 | Stage 1 |  | Kennewick | WA | 99336 | 76664 | 2017-02-21 | New, Alterations or New, Interior Completions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 5 |  |  | Yes | Yes | 19
16- 647514-1 | 16- 647514-1 | Unconditioned or no new HVAC |  | Port Townsend | WA | 98368 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 9.6
16- 654852-1 | 16- 654852-1 | Stage 1 |  | Seattle | WA | 98195 | 300000 | 2020-01-01 | New | School (University) | [5 empty] | Other | Unit heaters | Other | Terminal Units | Natural Gas | [6 empty] | 8 |  |  | Yes | Yes | 1
16- 656736-1 | 16- 656736-1 | Stage 1 |  | Bend | OR | 97703 | 4104 | 2017-12-21 | Alterations/Renovations, Interior Completions | Assembly | [5 empty] | Zonal Electric |  | None |  | Electric | [9 empty] | No | No | 21.3333
16- 657491-1 | 16- 657491-1 | Stage 2 |  | Portland | OR | 97202 | 56160 | 2017-04-29 | New | Multi-Family Residential | Portland, OR |  |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | Yes | No | 90.3333
16- 662436-1 | 16- 662436-1 | Stage 2 |  | Redmond | OR | 97756 | 56628 | 2016-06-10 | Alterations/Renovations, Interior Completions | Office | Redmond, OR |  |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Air Source Heat Pump (Packaged Rooftop) |  | Natural Gas |  |  | 3 | 1 | [5 empty] | No | No | 138
16- 665544-1 | 16- 665544-1 | Stage 1 |  | Nezperce | ID | 83543 | 12243 | 2016-04-26 | Alterations/Renovations, Interior Completions | Other | [5 empty] | Gas-fired indoor air handling unit | Gas furnace (M1.1 - page 41) | Direct Expansion Split System Air Handler | Split system condensing unit/central AC | Natural Gas | [9 empty] | No | No | 20.5
16- 666827-1 | 16- 666827-1 | Unconditioned or no new HVAC |  | Portland | OR | 97206 | 0 | 0 | New | School (K-12) | [21 empty] | 12.6667
16- 669048-1 | 16- 669048-1 | Unconditioned or no new HVAC |  | Great Falls | MT | 59405 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 3.5
16- 672346-1 | 16- 672346-1 | Unconditioned or no new HVAC |  | Beaverton | OR | 97005 | 0 | 0 | New | Office | [21 empty] | 3.2
16- 680124-1 | 16- 680124-1 | Stage 2 |  | Keizer | OR | 97303 | 40000 | 2017-02-27 | Alterations/Renovations, Interior Completions | Retail | Keizer, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 1 |  |  | No | No | 31.5
16- 684399-1 | 16- 684399-1 | Unconditioned or no new HVAC |  | Seattle | WA | 98199 | 0 | 0 | Alterations/Renovations, Additions | Hospital | [21 empty] | 9.6
16- 685200-2 | 16- 685200-2 | Stage 1 |  | Walla Walla | WA | 99362 | 82735 | 2018-04-09 | New, Alterations or New, Interior Completions | School (University) | Walla Walla |  |  |  |  | Other | Existing hot water system | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | No | No | 1
16- 685359-1 | 16- 685359-1 | Stage 1 |  | Rexburg | ID | 83440 | 49649 | 2016-08-17 | New | Multi-Family Residential | [5 empty] | Gas-fired indoor air handling unit | M-5, Indoor Upflow Furnace | Direct Expansion Split System Air Handler | M-5, DX Split System AC (indoor evaporator, Not RTU) | Natural Gas | [9 empty] | No | No | 21
16- 687637-1 | 16- 687637-1 | Stage 1 |  | Grandview | WA | 98930 | 194986 | 2018-08-22 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 4
16- 688614-1 | 16- 688614-1 | Stage 1 |  | Boise | ID | 83680 | 84900 | 2017-08-11 | New | Office | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas |  | 4 | 2 |  |  |  | 8 |  |  | No | Yes | 2.625
16- 688717-1 [RTU] | 16- 688717-1 | Stage 2 | RTU | Boise | ID | 83702 | 3526 | 2018-01-05 | New | Multi-Family Residential | Boise, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 2.353
16- 688717-1 [VRF] | 16- 688717-1 | Stage 2 | VRF | Boise | ID | 83702 | 2468 | 2018-01-05 | New | Multi-Family Residential | Boise, ID | 2012 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 4 |  |  |  | 1 |  |  | Yes | Yes | 1.647
16- 689024-1 | 16- 689024-1 | Stage 1 |  | Oregon City | OR | 97045 | 44523 | 2019-10-16 | Alterations/Renovations, Additions | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 1 |  |  | Yes | Yes | 7.25
16- 689616-1 | 16- 689616-1 | Stage 1 |  | Seattle | WA | 98109 | 650000 | 2021-06-01 | Alterations/Renovations, Additions | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas |  |  | 3 | [6 empty] | Yes | Yes | 1
16- 706094-1 | 16- 706094-1 | Stage 2 |  | Portland | OR | 97201 | 64200 | 2018-06-29 | New | Hospital | Portland, OR | 2014 OEESC |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 10 |  |  | Yes | Yes | 2.75
16- 709134-1 | 16- 709134-1 | Stage 2 |  | Pullman | WA | 99163 | 100755 | 2016-08-05 | New | Office | Pullman, WA | 2012 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 2 | [6 empty] | No | No | 2.625
16- 720532-1 | 16- 720532-1 | Stage 2 |  | Bothell | WA | 98021 | 4526 | 2016-06-06 | New | Restaurant | Bothell, WA | 2012 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 29
16- 727455-1 | 16- 727455-1 | Stage 2 |  | Beaverton | OR | 97005 | 99500 | 2017-07-11 | New | Residential Care | Beaverton, OR | 2014 OEESC | Total Building Performance |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric |  |  |  | 8 |  |  |  |  | 3 | Yes | No | 5.6667
16- 732678-1 | 16- 732678-1 | Project not completed |  | Newport/Walport | OR | 99156 | 0 | 0 | New | School (University) | [21 empty] | 7.25
16- 735523-1 [Boiler] | 16- 735523-1 | Stage 1 | Boiler | Sherwood | OR | 97140 | 350000 | 2018-03-28 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 0.5
16- 735523-1 [Classrooms, commons, misc.] | 16- 735523-1 | Stage 2 | Classrooms, commons, misc. | Sherwood | OR | 97140 | 350000 | 2018-03-28 | New | School (K-12) | Sherwood, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 19 |  |  | No | No | 0.5
17- 500861-2 | 17- 500861-2 | Stage 1 |  | Ellensburg | WA | 98926 | 39800 | 2017-02-28 | New | Multi-Family Residential | [5 empty] | Zonal Electric |  | Other | Individual Room AC - min efficiency | Electric | [9 empty] | No | No | 4
17- 508352-1 | 17- 508352-1 | Stage 1 |  | Tukwila | WA | 98168 | 28000 | 2018-09-05 | Alterations/Renovations, Additions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [5 empty] | 2 |  |  |  | Yes | Yes | 24.3333
17- 509238-1 | 17- 509238-1 | Stage 1 |  | Spokane | WA | 99201 | 23348 | 2018-05-18 | Alterations/Renovations, Interior Completions | Assembly | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 2 |  |  | Yes | No | 3.75
17- 521675-1 | 17- 521675-1 | Stage 2 |  | Portland | OR | 97210 | 90155 | 2018-09-07 | New | Multi-Family Residential | Portland, OR | 2014 OEESC | Prescriptive |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [6 empty] | 3 |  | 2 | Yes | No | 55
17- 527227-1 | 17- 527227-1 | Stage 1 |  | Bellevue | WA | 98004 | 94841 | 2018-03-14 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Other | Water-to-Water HP (WSHP), M004 | Natural Gas | [5 empty] | 1 | 1 |  |  | Yes | Yes | 12.6667
17- 535960-1 | 17- 535960-1 | Stage 1 |  | Tumwater | WA | 98512 | 14500 | 2019-03-19 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 1 |  |  | No | Yes | 68
17- 546146-2 | 17- 546146-2 | Unconditioned or no new HVAC |  | Vancouver | WA | 98661 | 0 | 0 | New, Alterations or New, Interior Completions | School (K-12) | [21 empty] | 24.3333
17- 550764-1 | 17- 550764-1 | Stage 2 |  | Portland | OR | 97202 | 6600 | 2017-10-13 | New | Lodging | Portland, OR |  | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [6 empty] | 3 |  |  | Yes | Yes | 7.75
17- 551538-3 | 17- 551538-3 | Stage 2 |  | Ramsay | MT | 59748 | 19999 | 2019-02-02 | New | Restaurant | Ramsay, MT | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | Yes | 8
17- 552951-1 | 17- 552951-1 | Stage 1 |  | Wheeler | OR | 97503 | 24600 | 2020-07-15 | Alterations/Renovations, Interior Completions | Hospital | [5 empty] | Other | Existing Boiler System, M6.2 & M5.2 | Air Cooled Chiller |  | Natural Gas | [6 empty] | 1 |  |  | No | No | 4.6
17- 571695-2 | 17- 571695-2 | Stage 2 |  | Redmond | WA | 98052 | 27860 | 2018-07-01 | New | Restaurant | Redmond, WA | 2015 WSEC | Prescriptive | More efficient HVAC | DOAS | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  | 2 | [6 empty] | Yes | Yes | 2.2
17- 584823-1 | 17- 584823-1 | Stage 2 |  | Bellevue | WA | 98007 | 69504 | 2017-11-01 | New, Additions | School (University) | Bellevue, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 6 |  |  |  | Yes | 7.25
17- 594224-1 | 17- 594224-1 | Stage 2 |  | Hoquiam | WA | 98550 | 3584 | 2017-07-11 | New, Alterations or New, Interior Completions | Office | Hoquiam, WA |  | Total Building Performance |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | No | 103.7143
17- 599945-1 | 17- 599945-1 | Unconditioned or no new HVAC |  | Meridian | ID | 83642 | 0 | 0 | New, Alterations or New, Interior Completions | School (K-12) | [21 empty] | 38.25
17- 604042-1 | 17- 604042-1 | Unconditioned or no new HVAC |  | Milwaukie | OR | 97267 | 0 | 0 | New | School (University) | [21 empty] | 2.2
17- 607886-1 | 17- 607886-1 | Stage 2 |  | Boise | ID | 83704 | 13111 | 2017-07-31 | New | Retail | Boise, ID | 2012 IECC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 1 | [6 empty] | No | No | 26.3333
17- 623990-1 | 17- 623990-1 | Unconditioned or no new HVAC |  | Baker City | OR | 97814 | 0 | 0 | Alterations/Renovations, Interior Completions | School (K-12) | [21 empty] | 38.25
17- 633318-2 | 17- 633318-2 | Stage 1 |  | Kennewick | WA | 99336 | 292000 | 2019-04-08 | New, Alterations or New, Interior Completions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 7 |  |  | Yes | Yes | 1
17- 634478-1 | 17- 634478-1 | Stage 2 |  | Portland | OR | 97213 | 29543 | 2017-07-06 | New | Multi-Family Residential | Portland, OR |  |  |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric |  |  |  | 2 |  |  |  |  | 1 | No | No | 90.3333
17- 635582-1 | 17- 635582-1 | Stage 2 |  | Hillsboro | OR | 97124 | 20424 | 2017-09-25 | Alterations/Renovations, Additions | Assembly | Hillsboro, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 123
17- 635972-2 [Cooling Tower] | 17- 635972-2 | Stage 1 | Cooling Tower | Boise | ID | 83712 | 151167 | 2018-02-15 | New | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [6 empty] | 18 |  | 2 | No | No | 1.3333
17- 635972-2 [Water Chiller] | 17- 635972-2 | Stage 1 | Water Chiller | Boise | ID | 83712 | 151167 | 2018-02-15 | New | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | No | No | 1.3333
17- 636076-1 | 17- 636076-1 | Stage 2 |  | Eugene | OR | 97401 | 293096 | 2018-05-16 | New | Multi-Family Residential | Eugene, OR | 2014 OEESC | Prescriptive |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric |  |  |  | 4 |  | 7 |  | 4 |  | No | No | 55
17- 637259-1 | 17- 637259-1 | Stage 2 |  | Hillsboro | OR | 97124 | 13201 | 2016-07-26 | Alterations/Renovations, Additions | Office | Hillsboro, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired indoor air handling unit |  | Air Source Heat Pump AHU (split system) |  | Natural Gas | [9 empty] | No | No | 103.7143
17- 642436-1 | 17- 642436-1 | Stage 2 |  | Eagle | ID | 83646 | 51933 | 2017-02-22 | New | Residential Care | Eagle, ID | 2015 IECC | Prescriptive | More Efficient HVAC |  | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas |  |  |  | 82 | [5 empty] | Yes | No | 3.75
17- 648782-2 | 17- 648782-2 | Stage 1 |  | Bellevue | WA | 98004 | 237000 | 2020-09-23 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas |  | 1 |  |  |  |  | 5 |  |  | Yes | Yes | 1.4
17- 653232-1 | 17- 653232-1 | Stage 2 |  | Bend | OR | 97701 | 10000 | 2018-01-01 | New, Additions | Retail | Bend, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 20.6
17- 655921-1 | 17- 655921-1 | Stage 1 |  | Spokane | WA | 99251 | 53942 | 2016-12-22 | New | Assembly | [5 empty] | Gas-fired indoor air handling unit |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 5 |  |  | Yes | Yes | 2.75
17- 662516-1 | 17- 662516-1 | Stage 1 |  | Klamath Falls | OR | 97601 | 100000 | 2018-05-04 | New | Office | [5 empty] | Other | District/Central Heating | Other | Chilled Water Plant | [10 empty] | No | No | 2.625
17- 672586-1 | 17- 672586-1 | Stage 2 |  | Boise | ID | 83704 | 84215 | 2017-05-10 | Alterations/Renovations, Interior Completions | Retail | Boise, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 26.3333
17- 674429-1 | 17- 674429-1 | Stage 2 |  | Coeur D Alene | ID | 83815 | 14000 | 2017-04-25 | Alterations/Renovations, Interior Completions | Assembly | Coeur D Alene, ID |  |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 32.75
17- 676005-1 | 17- 676005-1 | Stage 2 |  | Boise | ID | 83709 | 77431 | 2017-12-01 | New | Multi-Family Residential | Boise, ID |  |  |  |  | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | No | No | 9.6667
17- 685860-1 | 17- 685860-1 | Unconditioned or no new HVAC |  | Redmond | OR | 97756 | 0 | 0 | Alterations/Renovations, Interior Completions | Lodging | [21 empty] | 11.75
17- 686013-1 | 17- 686013-1 | Unconditioned or no new HVAC |  | La Pine | OR | 97739 | 0 | 0 | New | Retail | [21 empty] | 20.6
17- 686039-1 | 17- 686039-1 | Stage 2 |  | Rockaway Beach | OR | 97136 | 9221 | 2018-04-07 | New | Retail | Rockaway Beach, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 119
17- 686985-1 | 17- 686985-1 | Unconditioned or no new HVAC |  | Seattle | WA | 98104 | 0 | 0 | Alterations/Renovations, Additions | Other | [21 empty] | 20
17- 697310-1 | 17- 697310-1 | Stage 2 |  | Seattle | WA | 98112 | 7952 | 2017-02-07 | Alterations/Renovations, Interior Completions | Residential Care | Seattle, WA | 2015 SEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | No | Yes | 1.6
17- 701880-1 | 17- 701880-1 | Stage 2 |  | Bend/Tumalo | OR | 97701 | 10000 | 2018-06-08 | New | Other | Bend/Tumalo, OR | 2014 OEESC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [8 empty] | 1 | Yes | Yes | 2.4
17- 711287-2 | 17- 711287-2 | Stage 1 |  | Seaside | OR | 97138 | 38975 | 2020-09-01 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | yes | No | 8.5
17- 716517-1 | 17- 716517-1 | Stage 2 |  | Edmonds | WA | 98020 | 165 | 2017-05-23 | Alterations/Renovations, Interior Completions | Supermarket | Edmonds, WA | 2015 IECC | Prescriptive | More Efficient HVAC | Additional Efficiency Options | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 88
17- 719811-1 | 17- 719811-1 | Stage 2 |  | Boise | ID | 83702 | 43560 | 2018-08-31 | New | Lodging | Boise, ID | 2015 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  |  | 2 |  |  | 9 |  |  | No | No | 2
17- 727339-5 | 17- 727339-5 | Project not completed |  | Gig Harbor | WA | 98332 | 0 | 0 | New | Restaurant | [21 empty] | 2.2
17- 729343-1 | 17- 729343-1 | Stage 1 |  | Sequim | WA | 98382 | 1135 | 2021-05-05 | Alterations/Renovations, Additions | Office | [5 empty] | Air Source Heat Pump (Packaged Rooftop) |  | Air Cooled Chiller |  | Electric | [6 empty] | 1 |  |  | Yes | Yes | 61
17- 737174-1 | 17- 737174-1 | Stage 1 |  | Kalispell | MT | 59901 | 86663 | 2018-11-03 | New | Residential Care | [5 empty] | Other | Unit heaters | Other | Terminal Units | Natural Gas | [8 empty] | 1 | No | No | 6
17- 739244-1 | 17- 739244-1 | Stage 1 |  | White City | OR | 97503 | 35648 | 2019-01-07 | New | School (University) | [5 empty] | Boiler (Hot water or steam) | M101 Mechanical Schedule | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 2 |  |  |  | 2 |  |  | No | Yes | 10.6
17- 750195-1 | 17- 750195-1 | Unconditioned or no new HVAC |  | Seattle | WA | 98101 | 0 | 0 | Alterations/Renovations, Interior Completions | Restaurant | [21 empty] | 7.6667
17- 770324-1 | 17- 770324-1 | Unconditioned or no new HVAC |  | Coeur D Alene | ID | 83814 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 3.5
17- 775091-1 | 17- 775091-1 | Stage 1 |  | Ellensburg | WA | 98926 | 105000 | 2019-09-01 | New | Lodging | [5 empty] | Other | District steam heating system | Other | District chilled water | Natural Gas | [9 empty] | No | Yes | 2
17- 777891-1 [Common area] | 17- 777891-1 | Stage 2 | Common area | Meridian | ID | 83642 | 29634 | 2018-03-23 | New | Residential Care | Meridian, ID | 2015 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | Yes | Yes | 1.3265
17- 777891-1 [Living area] | 17- 777891-1 | Stage 1 | Living area | Meridian | ID | 83642 | 54138 | 2018-03-23 | New | Residential Care | [5 empty] | Packaged Terminal Heat Pump |  | Packaged Terminal Heat Pump |  | Electric | [9 empty] | Yes | Yes | 2.4235
17- 778018-1 | 17- 778018-1 | Stage 2 |  | Boise | ID | 83707 | 120000 | 2018-04-12 | New | Office | Boise, ID | 2015 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 2.625
17- 792314-1 | 17- 792314-1 | Stage 2 |  | Boise | ID | 83709 | 5593 | 2017-09-28 | Alterations/Renovations, Interior Completions | Restaurant | Boise, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 3.2
17- 793879-1 | 17- 793879-1 | Stage 1 |  | Kirkland | WA | 98033 | 46539 | 2018-06-04 | NEW | Supermarket | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 1 |  |  |  | Yes | Yes | 19
17- 799406-1 | 17- 799406-1 | Stage 2 |  | Meridian | ID | 83642 | 58164 | 2017-09-27 | New | Retail | Meridian, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 6 |  |  |  | 2 |  |  | No | No | 4.6667
17- 803573-1 [Misc.] | 17- 803573-1 | Stage 2 | Misc. | Mukilteo | WA | 98275 | 10500 | 2018-01-01 | New | Assembly | Mukilteo, WA | 2015 WSEC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric |  |  | 1 | [6 empty] | Yes | Yes | 12.12
17- 803573-1 [Pad] | 17- 803573-1 | Stage 2 | Pad | Mukilteo | WA | 98275 | 7000 | 2018-01-01 | New | Assembly | Mukilteo, WA | 2015 WSEC | Prescriptive |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric | [9 empty] | Yes | Yes | 8.08
17- 805340-1 | 17- 805340-1 | Stage 1 |  | Lakewood | WA | 98498 | 49776 | 2018-03-14 | New | Lodging | [5 empty] | Packaged Terminal Heat Pump |  | Packaged Terminal Heat Pump |  | Electric |  |  | 1 |  |  |  | 3 |  |  | Yes | No | 26.75
17- 808067-1 | 17- 808067-1 | Stage 2 |  | Boise | ID | 83709 | 5336 | 2017-03-10 | Alterations/Renovations, Interior Completions | Office | Boise, ID | 2012 IECC | Prescriptive |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric | [9 empty] | No | No | 138
17- 809290-1 | 17- 809290-1 | Stage 1 |  | Renton | WA | 98055 | 10000 | 2018-02-12 | New, Alterations or New, Interior Completions | Office | [5 empty] | Gas-fired indoor air handling unit |  | Other | Existing chilled water plant | Natural Gas | [9 empty] | Yes | Yes | 7.2
17- 809467-1 | 17- 809467-1 | Stage 1 |  | Portland | OR | 97204 | 180000 | 2018-06-10 | New | Lodging | PORTLAND |  |  |  |  | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas |  | 10 | [7 empty] | Yes | Yes | 2.75
17- 812120-1 | 17- 812120-1 | Stage 1 |  | Spokane | WA | 99016 | 242466 | 2021-08-01 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas |  |  |  |  | 1 |  | 8 |  |  | Yes | Yes | 1
17- 813087-1 | 17- 813087-1 | Stage 2 |  | Meridian | ID | 83642 | 50194 | 2017-01-19 | New | Residential Care | Meridian, ID |  |  |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | Yes | Yes | 6
17- 815466-1 | 17- 815466-1 | Stage 2 |  | Idaho Falls | ID | 83402 | 15551 | 2018-05-18 | Additions | Assembly | Idaho Falls, ID | 2015 IECC | Prescriptive | Additional Efficiency Options | Additional Efficiency Options | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 21.3333
17- 821806-1 | 17- 821806-1 | Stage 2 |  | Bothell | WA | 98011 | 7462 | 2017-12-05 | Alterations/Renovations, Additions | Residential Care | Bothell, WA | 2015 WSEC | Total Building Performance |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 1 |  |  |  | Yes | No | 12.3333
17- 825961-1 | 17- 825961-1 | Stage 1 |  | Kalispell | MT | 59901 | 33078 | 2017-07-24 | Alterations/Renovations, Interior Completions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 38.25
17- 828956-1 | 17- 828956-1 | Unconditioned or no new HVAC |  | Lakewood | WA | 98499 | 0 | 0 | Alterations/Renovations, Additions | Restaurant | [21 empty] | 16
17- 830379-1 | 17- 830379-1 | Stage 2 |  | Medford | OR | 97504 | 12000 | 2018-05-25 | New | Other | Medford, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 8 |  |  |  | 1 |  |  | No | No | 17
17- 832860-1 [Garage area] | 17- 832860-1 | Stage 1 | Garage area | Boise | ID | 83705 | 18000 | 2018-03-30 | Alterations/Renovations, Interior Completions | Other | [5 empty] | Boiler (Hot water or steam) |  | Fluid Cooler |  | Natural Gas | [9 empty] | No | Yes | 6.616
17- 832860-1 [Living area] | 17- 832860-1 | Stage 2 | Living area | Boise | ID | 83705 | 8300 | 2018-03-30 | Alterations/Renovations, Interior Completions | Other | Boise, ID | 2012 IECC | Total Building Performance |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 1 |  |  | No | Yes | 3.0507
17- 840060-1 | 17- 840060-1 | Project not completed |  | North Bend | WA | 98045 | 0 | 0 | New | Lodging | [21 empty] | 26.75
17- 855496-1 [Living] | 17- 855496-1 | Stage 1 | Living | Meridian | ID | 58549 | 5703 | 2018-11-01 | New | Other | [5 empty] | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 6 |  |  |  | 1 |  |  | Yes | Yes | 3.3452
17- 855496-1 [Shop] | 17- 855496-1 | Stage 1 | Shop | Meridian | ID | 83642 | 4526 | 2018-11-01 | New | Other | [5 empty] | Zonal Gas |  | None |  | Natural Gas | [9 empty] | No | No | 2.6548
17- 856087-1 | 17- 856087-1 | Stage 2 |  | Bellevue | WA | 98004 | 2254 | 2017-08-29 | Alterations/Renovations, Interior Completions | Lodging | Bellevue, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [5 empty] | 1 |  |  |  | Yes | Yes | 26.75
17- 859425-1 | 17- 859425-1 | Unconditioned or no new HVAC |  | Gresham | OR | 97030 | 0 | 0 | New | Office | [21 empty] | 61
17- 860845-1 | 17- 860845-1 | Stage 1 |  | Oakridge | OR | 97463 | 140000 | 2019-07-17 | Alterations/Renovations, Interior Completions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Source Heat Pump AHU (split system) |  | Natural Gas |  |  |  | 2 |  |  | 5 |  |  | Yes | No | 108.6667
17- 863159-1 | 17- 863159-1 | Stage 1 |  | Hood River | OR | 97031 | 32000 | 2018-11-16 | Alterations/Renovations, Interior Completions | School (K-12) | [5 empty] | Other | Existing hydronic heating (assumed) | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [8 empty] | 1 | No | No | 38.25
17- 866279-1 | 17- 866279-1 | Stage 2 |  | Kent | WA | 98032 | 3334 | 2018-05-19 | New | Restaurant | Kent, WA | 2015 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 7.6667
17- 867164-1 | 17- 867164-1 | Stage 1 |  | Kalispell | MT | 59901 | 28216 | 2017-02-20 | New | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas |  |  | 1 |  |  |  | 1 |  | 1 | No | No | 2.3333
17- 870836-1 | 17- 870836-1 | Stage 1 |  | Idaho Falls | ID | 83404 | 58889 | 2018-07-06 | Additions | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas |  |  | 3 | [6 empty] | No | No | 1
18- 510776-3 | 18- 510776-3 | Stage 1 |  | Bellevue | WA | 98004 | 425692 | 2018-01-30 | New | Restaurant | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [5 empty] | 5 |  |  |  | Yes | Yes | 2.2
18- 512733-1 | 18- 512733-1 | Unconditioned or no new HVAC |  | Spokane | WA | 99201 | 0 | 0 | Alterations/Renovations, Interior Completions | Restaurant | [21 empty] | 1
18- 527834-1 | 18- 527834-1 | Project not completed |  | Eugene | OR | 97401 | 0 | 0 | New | Lodging | [21 empty] | 1.4
18- 535655-1 | 18- 535655-1 | Stage 2 |  | Seattle | WA | 98133 | 4546 | 2018-09-11 | New | Restaurant | Seattle, WA | 2015 SEC | Prescriptive | Additional Efficiency Options | Additional Efficiency Options | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 16
18- 538933-1 | 18- 538933-1 | Stage 1 |  | Leavenworth | WA | 98826 | 13523 | 2017-04-28 | New | Restaurant | [5 empty] | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [5 empty] | 2 |  |  |  | No | No | 3.2
18- 542998-1 | 18- 542998-1 | Stage 2 |  | Aberdeen | ID | 83210 | 2000 | 2015-03-31 | New | School (University) | Bingham County |  | Prescriptive |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric | [9 empty] | No | No | 27.5
18- 554364-1 [Administrative] | 18- 554364-1 | Stage 2 | Administrative | Nampa | ID | 83686 | 16815 | 2017-11-03 | New | School (University) | Nampa, ID | 2012 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 2 |  |  | Yes | Yes | 1.3333
18- 554364-1 [Dining] | 18- 554364-1 | Stage 1 | Dining | Nampa | ID | 83686 | 16815 | 2017-11-03 | New | School (University) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | Yes | Yes | 1.3333
18- 554364-1 [Kitchen & Whitebox] | 18- 554364-1 | Stage 2 | Kitchen & Whitebox | Nampa | ID | 83686 | 16816 | 2017-11-03 | New | School (University) | Nampa, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 1.3334
18- 559771-1 | 18- 559771-1 | Stage 2 |  | Tonasket | WA | 98855 | 800 | 2018-06-30 | New | Hospital | Tonasket, WA |  |  |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 5.6667
18- 559908-1 | 18- 559908-1 | Unconditioned or no new HVAC |  | Rupert | ID | 83350 | 0 | 0 | Alterations/Renovations, Interior Completions | Hospital | [21 empty] | 5.6667
18- 560625-1 | 18- 560625-1 | Stage 2 |  | Portland | OR | 97214 | 12212 | 2019-02-13 | Alterations/Renovations, Interior Completions | Restaurant | Portland, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 6.5
18- 563561-1 | 18- 563561-1 | Stage 2 |  | Ritzville | WA | 99169 | 38000 | 2018-07-20 | Alterations/Renovations, Additions | School (K-12) | Ritzville, WA | 2015 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | Yes | 29
18- 564051-1 | 18- 564051-1 | Stage 1 |  | Burns | OR | 97720 | 2757 | 2018-01-01 | Alterations/Renovations, Additions | Other | [5 empty] | Other | Propane water heater | Other | Evaporative Cooler | Other | Propane | [8 empty] | Yes | No | 27.5
18- 568981-1 | 18- 568981-1 | Stage 1 |  | Spokane | WA | 99208 | 120000 | 2019-01-30 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 3 |  |  | Yes | Yes | 4
18- 571936-1 | 18- 571936-1 | Stage 2 |  | Twin Falls | ID | 83301 | 3760 | 2017-07-19 | New | Multi-Family Residential | Twin Falls, ID | 2012 IECC | Prescriptive |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | No | 34
18- 576787-1 | 18- 576787-1 | Stage 2 |  | Kelso | WA | 98626 | 8825 | 2018-06-29 | New | Other | Cowlitz County | 2015 IECC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | Yes | Yes | 17
18- 577317-1 | 18- 577317-1 | Stage 2 |  | Gig Harbor | WA | 98329 | 11550 | 2019-11-01 | New | Office | Gig Harbor, WA | 2015 WSEC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 103.7143
18- 585712-1 | 18- 585712-1 | Stage 2 |  | Victor | MT | 59875 | 47885 | 2018-03-16 | New | Office | Victor, MT | 2012 IECC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 48
18- 595441 | 18- 595441 | Stage 2 |  | Meridian | ID | 83646 | 10070 | 2018-01-01 | New, Additions | Hospital | Meridian, ID | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 5.6667
18- 596289-1 | 18- 596289-1 | Stage 2 |  | Kalispell | MT | 59901 | 19550 | 2018-02-13 | New | Retail | Kalispell, MT | 2012 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 1 |  |  | No | No | 18
18- 596300-1 | 18- 596300-1 | Stage 2 |  | Kalispell | MT | 59901 | 55053 | 2017-02-13 | Alterations/Renovations, Interior Completions | Retail | Kalispell, MT | 2012 IECC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 4.6667
18- 597863-1 [Data Center 1] | 18- 597863-1 | Stage 1 | Data Center 1 | Salem | OR | 97301 | 22935 | 2018-10-09 | Alterations/Renovations, Interior Completions | Assembly | Salem | 2014 OEESC |  |  |  | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [8 empty] | 1 | No | No | 8.25
18- 597863-1 [Data Center 2] | 18- 597863-1 | Stage 1 | Data Center 2 | Salem | OR | 97301 | 22935 | 2018-10-09 | Alterations/Renovations, Interior Completions | Assembly | Salem | 2014 OEESC |  |  |  | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [9 empty] | No | No | 8.25
18- 603716-1 | 18- 603716-1 | Stage 1 |  | Klamath Falls | OR | 97601 | 101000 | 2019-03-15 | Alterations/Renovations, Interior Completions | School (University) | [5 empty] | Other | Existing gas fired boiler | Direct Expansion Split System Air Handler |  | Natural Gas | [9 empty] | Yes | No | 14.5
18- 604780-1 | 18- 604780-1 | Unconditioned or no new HVAC |  | Ketchum | ID | 83340 | 0 | 0 | Alterations/Renovations, Additions | Assembly | [21 empty] | 3.75
18- 612115-1 | 18- 612115-1 | Stage 2 |  | Yachats | OR | 97498 | 12700 | 2018-05-19 | New | Other | Yachats, OR |  |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | No | 20
18- 614250-1 | 18- 614250-1 | Stage 2 |  | Seattle | WA | 98195 | 24857 | 2019-05-20 | Alterations/Renovations, Additions | Hospital | Seattle, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [6 empty] | 2 |  | 2 | Yes | Yes | 2.75
18- 625157-1 | 18- 625157-1 | Stage 2 |  | Seattle | WA | 98109 | 153463 | 2019-01-01 | Alterations/Renovations, Interior Completions | Lodging | Seattle, WA | 2015 SEC | Prescriptive |  |  | Packaged Terminal Heat Pump |  | Direct Expansion Packaged Rooftop HVAC |  | Electric | [9 empty] | Decoupled | No | 26.75
18- 625974-1 | 18- 625974-1 | Stage 2 |  | Redmond | OR | 97753 | 89575 | 2019-07-11 | New | Lodging | Redmond, OR | 2012 IECC | Prescriptive |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric |  |  | 1 |  |  |  | 2 | 1 |  | Yes | No | 10
18- 637948-1 | 18- 637948-1 | Stage 1 |  | Portland | OR | 97201 | 195150 | 2018-04-06 | Alterations/Renovations, Interior Completions | Hospital | [5 empty] | Other | AHU - HW coil connected to existing hydronic system | Other | AHU - CW coil connected to existing hydronic system | Natural Gas | [9 empty] | No | No | 9.6
18- 641038-2 | 18- 641038-2 | Project not completed |  | Portland | OR | 97205 | 0 | 0 | New | Lodging | [21 empty] | 1.4
18- 641081-1 | 18- 641081-1 | Stage 2 |  | East Wenatchee | WA | 98802 | 41017 | 2018-07-23 | New | Office | East Wenatchee, WA | 2015 WSEC | Prescriptive |  |  | Zonal Electric |  | Direct Expansion Split System Air Handler |  | Electric | [9 empty] | No | No | 3
18- 644665-1 | 18- 644665-1 | Stage 1 |  | Prosser | WA | 99350 | 157000 | 2021-06-12 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [5 empty] | 6 | 10 |  |  | Yes | Yes | 4
18- 650512-1 | 18- 650512-1 | Stage 2 |  | SeaTac | WA | 98188 | 1609 | 2020-01-01 | New | Office | SeaTac, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 26.3333
18- 662440-1 | 18- 662440-1 | Stage 1 |  | Salem | OR | 97301 | 42352 | 2020-02-07 | Alterations/Renovations, Interior Completions | Other | [5 empty] | Other | District Hot Water or Steam | Other | District Chilled Water | Natural Gas |  |  | 1 |  |  |  | 1 |  |  | No | Yes | 2.3333
18- 704117-1 | 18- 704117-1 | Stage 2 |  | Boise | ID | 83726 | 26000 | 2019-08-30 | New | Office | Boise, ID | 2015 IECC | Total Building Performance |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 3
18- 713902-1 | 18- 713902-1 | Unconditioned or no new HVAC |  | Oregon City | OR | 97045 | 0 | 0 | Alterations/Renovations, Additions | Hospital | [21 empty] | 9.6
18- 718226-1 [AHU] | 18- 718226-1 | Stage 2 | AHU | Boise | ID | 83726 | 29740 | 2018-04-19 | New | Hospital | Boise, ID | 2015 IECC | Prescriptive |  |  | Other | VAV AHU with electric heat | Direct Expansion Packaged Rooftop HVAC |  | Electric | [9 empty] | Yes | Yes | 1.4
18- 718226-1 [DHP] | 18- 718226-1 | Stage 2 | DHP | Boise | ID | 83726 | 19826 | 2018-04-19 | New | Hospital | Boise, ID | 2015 IECC | Prescriptive |  |  | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | Yes | Yes | 0.93331
18- 718902-1 | 18- 718902-1 | Stage 2 |  | Aumsville | OR | 97325 | 23000 | 2018-08-19 | New | Assembly | Marion County | 2009 IECC | Prescriptive |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | Yes | 123
18- 723839-1 | 18- 723839-1 | Stage 2 |  | Ellensburg | WA | 98926 | 8000 | 2018-06-12 | New | Lodging | Ellensburg, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  |  | 1 |  |  | 2 |  |  | Yes | Yes | 16
18- 735699-1 | 18- 735699-1 | Stage 1 |  | Sun Valley | ID | 83353 | 30319 | 2018-07-06 | New | Lodging | [5 empty] | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | No | 11.75
18- 736200-1 | 18- 736200-1 | Stage 1 |  | Kelso | WA | 98626 | 163000 | 2019-07-19 | New | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 2 |  |  | No | No | 12.6667
18- 737861-1 | 18- 737861-1 | Stage 2 |  | Pasco | WA | 99301 | 14142 | 2018-08-14 | New | Lodging | Pasco, WA |  |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric |  |  |  | 2 | 3 |  | 2 |  |  | Yes | No | 11.75
18- 765134-1 | 18- 765134-1 | Stage 1 |  | Meridian | ID | 83642 | 60751 | 2019-01-25 | Alterations/Renovations, Interior Completions | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 3.5
18- 768226-1 | 18- 768226-1 | Stage 1 |  | Ketchum | ID | 83340 | 12215 | 2018-11-07 | Additions | Restaurant | [5 empty] | Boiler (Hot water or steam) |  | Cooling Tower |  | Natural Gas | [8 empty] | 2 | Yes | No | 8
18- 785631-1 | 18- 785631-1 | Stage 2 |  | Boise | ID | 83716 | 1185 | 2018-03-06 | Alterations/Renovations, Interior Completions | Restaurant | Boise, ID | 2015 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 2.25
18- 788447-1 | 18- 788447-1 | Unconditioned or no new HVAC |  | Hillsboro | OR | 97124 | 0 | 0 | Alterations/Renovations, Additions | Office | [21 empty] | 103.7143
18- 792246-1 | 18- 792246-1 | Stage 1 |  | Meridian | ID | 83646 | 23076 | 2018-03-01 | New | Residential Care | [5 empty] | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas |  |  |  | 1 | [5 empty] | No | No | 7
18- 808485-1 | 18- 808485-1 | Stage 1 |  | Vancouver | WA | 98661 | 14469 | 2019-05-31 | New | Retail | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 5 |  |  | Yes | No | 2
18- 811956-1 | 18- 811956-1 | Stage 2 |  | Yakima | WA | 98901 | 4600 | 2019-06-01 | Alterations/Renovations, Additions | Other | Yakima, WA |  |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | Yes | No | 20.5
18- 823343-1 | 18- 823343-1 | Unconditioned or no new HVAC |  | Auroroa | OR | 97002 | 0 | 0 | New | Office | [21 empty] | 103.7143
18- 832169-1 | 18- 832169-1 | Unconditioned or no new HVAC |  | Seattle | WA | 98104 | 0 | 0 | Alterations/Renovations, Additions | Office | [21 empty] | 103.7143
18- 863366-1 | 18- 863366-1 | Stage 2 |  | Cove | OR | 97824 | 5120 | 2019-06-24 | New | Restaurant | Cove, OR | 2014 OEESC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 3.2
18- 863748-1 | 18- 863748-1 | Stage 2 |  | Seattle | WA | 98122 | 10945 | 2018-03-14 | Alterations/Renovations, Additions | School (University) | Seattle, WA | 2015 SEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [5 empty] | 4 |  |  |  | No | Yes | 40
18- 865230-2 | 18- 865230-2 | Stage 1 |  | Seattle | WA | 98107 | 24000 | 2019-12-07 | New | Restaurant | [5 empty] | Air Source Heat Pump (Packaged Rooftop) | Heat Pump with Auxiliary Electric Heating | Air Source Heat Pump (Packaged Rooftop) |  | Electric | [6 empty] | 6 |  |  | Yes | No | 2.2
18- 899620-1 | 18- 899620-1 | Stage 2 |  | Meridian | ID | 83642 | 31944 | 2018-08-01 | New | Assembly | Meridian, ID | 2015 IECC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 9.5
18- 902490-4 | 18- 902490-4 | Stage 1 |  | Portland | OR | 97217 | 460000 | 2019-09-16 | New, Alterations or New, Interior Completions | Restaurant | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas |  | 6 | [7 empty] | No | No | 2.2
18- 908206-1 | 18- 908206-1 | Stage 2 |  | Boise | ID | 83706 | 3942 | 2018-09-07 | Additions | Retail | Boise, ID | 2015 IECC | Prescriptive |  |  | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric | [9 empty] | No | No | 20.6
18- 911270-3 | 18- 911270-3 | Unconditioned or no new HVAC |  | Maple Valley | WA | 98038 | 0 | 0 | New | Restaurant | [21 empty] | 16
19- 506267-1 | 19- 506267-1 | Stage 2 |  | Walla Walla | WA | 99362 | 141000 | 2020-07-07 | New | Multi-Family Residential | Walla Walla, WA |  |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric |  |  | 4 | 2 |  |  | 1 |  |  | No | No | 4
19- 510137-1 | 19- 510137-1 | Stage 1 |  | Tacoma | WA | 98405 | 14600 | 2021-01-01 | Alterations/Renovations, Additions | Hospital | [5 empty] | Other | New VAV AHUs connected to existing heating water system | Other | New VAV AHUs connected to existing chilled water system | Natural Gas | [9 empty] | Yes | No | 4.6
19- 520369-1 | 19- 520369-1 | Stage 1 |  | Selah | WA | 98942 | 20293 | 2018-11-30 | Alterations/Renovations, Interior Completions | Restaurant | [5 empty] | Gas-fired indoor air handling unit |  | Direct Expansion Split System Air Handler |  | Natural Gas |  |  | 3 | [6 empty] | No | No | 3.2
19- 544116-1 | 19- 544116-1 | Stage 1 |  | Seattle | WA | 98119 | 239875 | 2019-10-09 | New | Office | [5 empty] | Other | Heat Recovery Chiller, PG 153, Approved Plan Set 6566041-LastPhase, S:\Shared Folders\CADEO\03_Projects\BPA_MSA_2\TO032_Com HVAC Data Collection\Task 3 Implement Data Collection\Permit Files\Files from AHJs\Seattle Permits Upload\Follow-up Pt2.zip\Follow-up Pt2\6566041-PH | Other | Heat Recovery Chiller, PG 153, Approved Plan Set 6566041-LastPhase, S:\Shared Folders\CADEO\03_Projects\BPA_MSA_2\TO032_Com HVAC Data Collection\Task 3 Implement Data Collection\Permit Files\Files from AHJs\Seattle Permits Upload\Follow-up Pt2.zip\Follow-up Pt2\6566041-PH | Electric |  |  |  |  | 1 |  |  |  |  | Yes | Yes | 3.2
19- 550436-1 | 19- 550436-1 | Stage 2 |  | Ellensburg | WA | 98926 | 48153 | 2019-02-04 | Alterations/Renovations, Additions | Other | Ellensburg, WA | 2015 WSEC | Prescriptive | More efficient HVAC | DOAS | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [9 empty] | Yes | Yes | 6
19- 563281-1 [Boiler] | 19- 563281-1 | Stage 1 | Boiler | Somers | MT | 59932 | 12901.35 | 2019-02-13 | Alterations/Renovations, Additions | School (K-12) | [5 empty] | Boiler (Hot water or steam) |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | Yes | No | 18.15
19- 563281-1 [RTU] | 19- 563281-1 | Stage 1 | RTU | Somers | MT | 59932 | 10555.65 | 2019-02-13 | Alterations/Renovations, Additions | School (K-12) | [5 empty] | Air to Water Heat Pump |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [6 empty] | 3 |  |  | Yes | Yes | 14.85
19- 578698-1 | 19- 578698-1 | Project not completed |  | Boise | ID | 83725 | 0 | 0 | New | Retail | [21 empty] | 20.6
19- 608920-1 | 19- 608920-1 | Unconditioned or no new HVAC |  | Seattle | WA | 98104 | 0 | 0 | Alterations/Renovations, Interior Completions | Other | [21 empty] | 20
19- 626713-1 | 19- 626713-1 | Unconditioned or no new HVAC |  | Cascade Locks | OR | 97014 | 0 | 0 | Alterations/Renovations, Additions | Assembly | [21 empty] | 32.75
19- 666292-1 | 19- 666292-1 | Unconditioned or no new HVAC |  | Bend | OR | 97702 | 0 | 0 | New | School (K-12) | [21 empty] | 1
19- 669605-1 | 19- 669605-1 | Stage 1 |  | Athol | ID | 83801 | 612 | 2019-05-21 | New, Alterations or New, Interior Completions | Lodging | [5 empty] | Zonal Electric |  | None |  | Electric | [9 empty] | No | No | 16
19- 672421-1 | 19- 672421-1 | Stage 2 |  | Kirkland | WA | 98034 | 690 | 2018-06-26 | Additions | Residential Care | Kirkland, WA | 2015 WSEC | Prescriptive | More efficient HVAC | Additional Efficiency Options | Ductless Heat Pump |  | Ductless Heat Pump |  | Electric | [9 empty] | No | No | 12.3333
19- 696068-1 | 19- 696068-1 | Stage 1 |  | Idaho Falls | ID | 83404 | 3100 | 2019-04-15 | Alterations/Renovations, Interior Completions | Retail | [5 empty] | Other | Existing hydronic heating / new VAV terminal units | Other | Assumed existing DX RTU (VAV System). TI Only, no new cooling. | Electric | [9 empty] | No | No | 26.3333
19- 700419-1 | 19- 700419-1 | Stage 2 |  | Meridian | ID | 83642 | 108117 | 2017-06-26 | Alterations/Renovations, Interior Completions | Retail | Meridian, ID | 2012 IECC | Total Building Performance |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas |  |  | 6 | [6 empty] | Yes | No | 4
19- 703964-1 | 19- 703964-1 | Stage 1 |  | Antelope | OR | 97001 | 19009 | 2019-05-10 | New | Lodging | [5 empty] | Boiler (Hot water or steam) |  | Water Cooled Chiller |  | Natural Gas | [9 empty] | Yes | Yes | 16
19- 719739-1 | 19- 719739-1 | Stage 2 |  | Spokane | WA | 99208 | 7163 | 2020-01-20 | New | Restaurant | Spokane, WA | 2015 WSEC | Prescriptive |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 3.2
19- 730078-1 | 19- 730078-1 | Stage 2 |  | Meridian | ID | 83642 | 141013 | 2020-01-06 | New | Office | Meridian, ID | 2015 IECC | Prescriptive | More Efficient HVAC | More Efficient HVAC | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [5 empty] | 5 | 5 |  |  | Yes | Yes | 2.625
19- 731945-1 | 19- 731945-1 | Stage 2 |  | Yakima | WA | 98902 | 19608 | 2021-01-07 | Alterations/Renovations, Interior Completions | School (University) | Yakima, WA | 2015 WSEC | Prescriptive | More efficient HVAC | DOAS | Air Source Heat Pump (Packaged Rooftop) |  | Air Source Heat Pump (Packaged Rooftop) |  | Electric | [6 empty] | 5 |  |  | Yes | Yes | 6
19- 736182-1 | 19- 736182-1 | Stage 1 |  | Goldendale | WA | 98620 | 126000 | 2020-07-01 | New | Other | [5 empty] | Other | Wood stove | None |  | Other | Wood | [10 empty] | 138
19- 765123-1 | 19- 765123-1 | Stage 2 |  | Silverton | OR | 97381 | 4166 | 2020-01-01 | New | Office | Silverton, OR | 2014 OEESC |  |  |  | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | No | 103.7143
19- 766177-1 | 19- 766177-1 | Unconditioned or no new HVAC |  | Caldwell | ID | 83651 | 0 | 0 | Alterations/Renovations, Interior Completions | Retail | [21 empty] | 4
19- 773267-1 | 19- 773267-1 | Unconditioned or no new HVAC |  | The Dalles | OR | 97058 | 0 | 0 | Alterations/Renovations, Interior Completions | Office | [21 empty] | 2.625
19- 787006-1 | 19- 787006-1 | Stage 1 |  | McCall | ID | 83638 | 148441 | 2021-05-04 | Alterations/Renovations, Additions | Hospital | [5 empty] | Boiler (Hot water or steam) |  | Air Cooled Chiller |  | Natural Gas | [6 empty] | 3 |  |  | No | No | 2.6667
19- 820425-1 | 19- 820425-1 | Stage 2 |  | Wenatchee | WA | 98801 | 41846 | 2019-07-02 | New | Lodging | Wenatchee, WA | 2015 WSEC | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric |  |  |  | 1 |  |  | 1 |  |  | No | No | 11.75
19- 821533-1 | 19- 821533-1 | Stage 1 |  | Missoula | MT | 59802 | 22454 | 2019-10-18 | Additions | Hospital | [5 empty] | Other | Existing heated water | Other | Existing chilled water | Natural Gas | [6 empty] | 1 |  |  | No | No | 3.5
19- 850137-1 | 19- 850137-1 | Stage 1 |  | Portland | OR | 97225 | 46000 | 2019-08-30 | New | Assembly | [5 empty] | Boiler (Hot water or steam) | M0.02 HVAC Schedules | Direct Expansion Split System Air Handler |  | Natural Gas |  | 1 |  |  |  |  | 1 |  |  | No | No | 20.2
19- 912980-1 | 19- 912980-1 | Stage 2 |  | Pullman | WA | 99163 | 2123 | 2019-09-18 | New | Multi-Family Residential | Pullman, WA | 2015 WSEC | Prescriptive | High efficiency water heating | More efficient HVAC | Air Source Heat Pump AHU (split system) |  | Air Source Heat Pump AHU (split system) |  | Electric | [9 empty] | No | No | 21
19- 933769-1 | 19- 933769-1 | Stage 1 |  | Bellevue | WA | 98004 | 40200 | 2018-08-20 | Alterations/Renovations, Interior Completions | Restaurant | [5 empty] | Other | Existing condenser water loop connecting to new WSHP | Other | Existing condenser water loop connecting to new WSHP | Natural Gas | [9 empty] | Yes | No | 7.6667
19- 937126-1 | 19- 937126-1 | Stage 2 |  | Vancouver | WA | 98662 | 5048 | 2021-01-07 | New | Restaurant | Vancouver, WA | 2015 WSEC |  |  |  | Gas-fired Packaged Rooftop HVAC |  | Direct Expansion Packaged Rooftop HVAC |  | Natural Gas | [9 empty] | No | No | 29
98- 661137-1 | 98- 661137-1 | Project not completed |  | Tualatin | OR | 97062 | 0 | 0 | New, Add, Alt or New, Add, Interior Completions | Hospital | [21 empty] | 1.2
98- 927699-1 | 98- 927699-1 | Stage 2 |  | Portland | OR | 97204 | 161000 | 2015-05-07 | New | Lodging | Portland, OR |  | Prescriptive |  |  | Variable Refrigerant Flow |  | Variable Refrigerant Flow |  | Electric | [5 empty] | 1 | 4 |  |  | Yes | Yes | 2.75

## Stage2Heating
Project_ID | Equipment Type | Equipment ID | Manufacturer | Model | Capacity_Metric_1 | Capacity_Metric_1_Units | Capacity_Metric_2 | Capacity_Metric_2_Units | Efficiency_Metric_1 | Efficiency_Metric_1_Units | Efficiency_Metric_2 | Efficiency_Metric_2_Units | Efficiency_Metric_3 | Efficiency_Metric_3_Units | Fuel Type | Equipment_Type_Other | Cap_met_other | Cap_met_other_units | Eff_met_other | Eff_met_other_units | HP Includes Auxiliary Heat? | Size of Aux Heat
07- 782313-1 | Variable Refrigerant Flow | HP-CS | Mitsubishi | PURY-P96 | 80 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
07- 782313-1 | Variable Refrigerant Flow | HP-K | Mitsubishi | PURY-P168 | 80 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
07- 782313-1 | Variable Refrigerant Flow | HP-K2 | Mitsubishi | PURY-P336 | 320 | MBH |  |  | 3.52 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
07- 782313-1 | Variable Refrigerant Flow | HP-K3 | Mitsubishi | PURY-P336 | 320 | MBH |  |  | 3.52 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
07- 782313-1 | Variable Refrigerant Flow | HP-K4 | Mitsubishi | PURY-P72 | 80 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
07- 782313-1 | Variable Refrigerant Flow | HP-P | Mitsubishi | PURY-P144 | 80 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
09- 581175-1 | Variable Refrigerant Flow | ODU | Mitsubishi | PURY-P-240TSMU-A | 270 | MBH |  |  | 3.41 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
11- 468179-1 | Ductless Heat Pump | DHP-1 | Daikin | FTXS24LVJU | 25400 | Btu/hr |  |  | 10.6 | HSPF | 3.37 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
11- 468179-1 | Ductless Heat Pump | DHP-2 | Daikin | FTXS24LVJU | 25400 | Btu/hr |  |  | 10.6 | HSPF | 3.37 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
11- 468179-1 | Ductless Heat Pump | DHP-3 | Daikin | FTXS24LVJU | 25400 | Btu/hr |  |  | 10.6 | HSPF | 3.37 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
11- 531122-1 | Ductless Heat Pump | HP-1 | Daikin | FXAQ | 49.5 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
11- 531122-1 | Ductless Heat Pump | HP-2 | Daikin | FXAQ | 49.5 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-01 | Trane | 4TVR0240B300NB | 270000 | Btu/hr |  |  | 3.24 | COP(47) | 2.4 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-02 | Trane | 4TVR0168B400NB | 189000 | Btu/hr |  |  | 3.46 | COP(47) | 2.43 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-03 | Trane | 4TVR0144B300NB | 162000 | Btu/hr |  |  | 3.56 | COP(47) | 2.23 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-04 | Trane | 4TVR0120B300NB | 135000 | Btu/hr |  |  | 3.43 | COP(47) | 2.45 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-05 | Trane | 4TVR0168B400NB | 189000 | Btu/hr |  |  | 3.46 | COP(47) | 2.43 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-06 | Trane | 4TVR0144B300NB | 162000 | Btu/hr |  |  | 3.54 | COP(47) | 2.23 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-07 | Trane | 4TVR0168B400NB | 189000 | Btu/hr |  |  | 3.46 | COP(47) | 2.43 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-08 | Trane | 4TVR0144B300NB | 162000 | Btu/hr |  |  | 3.54 | COP(47) | 2.23 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-09 | Trane | 4TVR0168B400NB | 189000 | Btu/hr |  |  | 3.46 | COP(47) | 2.43 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-10 | Trane | 4TVR0144B300NB | 162000 | Btu/hr |  |  | 3.54 | COP(47) | 2.23 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-11 | Trane | 4TVR0168B400NB | 189000 | Btu/hr |  |  | 3.46 | COP(47) | 2.43 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-12 | Trane | 4TVR0144B300NB | 162000 | Btu/hr |  |  | 3.54 | COP(47) | 2.23 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 631833-2 | Variable Refrigerant Flow | ACCU-13 | Trane | 4TVR0120B300NB | 135000 | Btu/hr |  |  | 3.43 | COP(47) | 2.45 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
11- 656138-1 | Other | AHU-1 | Guardian | MX16CN21 | [10 empty] | Electric | Central electric coil | 5.6 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-10 | Guardian | MX20DN21 | [10 empty] | Electric | Central electric coil | 10.8 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-11 | Guardian | MX20DN21 | [10 empty] | Electric | Central electric coil | 10.8 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-2 | Guardian | MX20DN21 | [10 empty] | Electric | Central electric coil | 10.8 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-3 | Guardian | MX16CN21 | [10 empty] | Electric | Central electric coil | 7.2 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-4 | Guardian | MX16CN21 | [10 empty] | Electric | Central electric coil | 7.2 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-5 | Guardian | MX20DN21 | [10 empty] | Electric | Central electric coil | 10.8 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-6 | Guardian | MX16CN21 | [10 empty] | Electric | Central electric coil | 5.6 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-7 | Guardian | MX20DN21 | [10 empty] | Electric | Central electric coil | 10.8 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-8 | Guardian | MX16CN21 | [10 empty] | Electric | Central electric coil | 5.6 | kW | 1 | COP | N/A | N/A
11- 656138-1 | Other | AHU-9 | Guardian | MX20DN21 | [10 empty] | Electric | Central electric coil | 10.8 | kW | 1 | COP | N/A | N/A
12- 701660-1 | Variable Refrigerant Flow | HP-N1 | Mitsubishi | PURY-P288TSKML | 24 | Tons |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
12- 701660-1 | Variable Refrigerant Flow | HP-N2 | Mitsubishi | PURY-P192TSKML | 16 | Tons |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
12- 701660-1 | Variable Refrigerant Flow | HP-S1 | Mitsubishi | PURY-P288TSKML | 24 | Tons |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
12- 701660-1 | Variable Refrigerant Flow | HP-S2 | Mitsubishi | PURY-P192TSKML | 16 | Tons |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-1 | Daikin | REYQ288TAYDU | 256 | Btu/hr |  |  | 3.51 | COP(47) | 2.41 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-2 | Daikin | REYQ240TAYDU | 224 | Btu/hr |  |  | 3.68 | COP(47) | 2.27 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-3 | Daikin | REYQ192TAYDU | 183 | Btu/hr |  |  | 3.85 | COP(47) | 2.41 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-4 | Daikin | REYQ192TAYDU | 183 | Btu/hr |  |  | 3.85 | COP(47) | 2.41 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-5 | Daikin | REYQ168TAYDU | 134 | Btu/hr |  |  | 3.7 | COP(47) | 2.22 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-6 | Daikin | REYQ120TAYDU | 107 | Btu/hr |  |  | 4 | COP(47) | 2.46 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-7 | Daikin | REYQ96TAYDU | 89 | Btu/hr |  |  | 4.21 | COP(47) | 2.71 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 404186-1 | Variable Refrigerant Flow | HP-R-8 | Daikin | REYQ72TAYDU | 72 | Btu/hr |  |  | 3.88 | COP(47) | 2.49 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
13- 636582-1 | Gas-fired Packaged Rooftop HVAC | RT-1 | Carrier | 48P3L100 | 784 | MBH | 38520 | CFM | 80 | Thermal Efficiency (%) |  |  | 135 | HP | Natural Gas | [5 empty] | N/A | N/A
13- 636582-1 | Gas-fired Packaged Rooftop HVAC | RT-2 | Carrier | 48P3L100 | 784 | MBH | 40000 | CFM | 80 | Thermal Efficiency (%) |  |  | 135 | HP | Natural Gas | [5 empty] | N/A | N/A
13- 636582-1 | Gas-fired Packaged Rooftop HVAC | RT-4 | Trane | 4YCC3018 | 32 | MBH | 440 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.083333 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 426751-1 | Variable Refrigerant Flow | HP-1A | Mitsubishi | PURY-P144TLMU | 160 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 426751-1 | Variable Refrigerant Flow | HP-1B | Mitsubishi | PURY-P144TLMU | 160 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H1 | Daikin | REYQ456TYDN | 513000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H10 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H11 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H12 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H13 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H2 | Daikin | REYQ456TYDN | 513000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H3 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H4 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H5 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H6 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H7 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H8 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-H9 | Daikin | REYQ288TYDN | 324000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-L1 | Daikin | REYQ312TYDN | 351000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-L2 | Daikin | REYQ312TYDN | 351000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-L3 | Daikin | REYQ432TYDN | 486000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-L4 | Daikin | REYQ432TYDN | 486000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-L5 | Daikin | REYQ432TYDN | 486000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 493663-2 | Variable Refrigerant Flow | VRV-L6 | Daikin | REYQ432TYDN | 486000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Lennox | KGB048S4D | 52 | MBH | 1500 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Lennox | KGB060S4D | 52 | MBH | 1900 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Lennox | KGB036S4D | 52 | MBH | 1275 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-12 | Lennox | KGB060S4D | 52 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-13 | Lennox | KGB036S4D | 52 | MBH | 1150 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-14 | Lennox | KGB030S4D | 52 | MBH | 1000 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.25 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-15 | Lennox | KGB030S4D | 52 | MBH | 1000 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.25 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-16 | Lennox | KGB060S4D | 52 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Lennox | KGB048S4D | 52 | MBH | 1450 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Lennox | KGB048S4D | 52 | MBH | 1600 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Lennox | KGB048S4D | 52 | MBH | 1650 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Lennox | KGB060S4D | 52 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Lennox | KGB036S4D | 52 | MBH | 1150 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Lennox | KGA072S4B | 52 | MBH | 2475 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Lennox | KGB036S4D | 52 | MBH | 1225 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 494803-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Lennox | KGB030S4D | 52 | MBH | 975 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.25 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-1 | Mitsubishi | MXZ-8B48NA | 40.5 | MBH |  |  | 8.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-10 | Mitsubishi | SUZ-KA15NA | 18 | MBH |  |  | Unknown | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-2 | Carrier | 25HCD330A005 | 23.8 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-3 | Carrier | 25HCD348A005 | 46 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-4 | Carrier | 25HCD330A005 | 28.2 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-5 | Carrier | 25HCD336A005 | 34.4 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-6 | Carrier | 25HCD336A005 | 34.4 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-7 | Mitsubishi | PUZ-A24NHA4 | 18 | MBH |  |  | 10.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [DHP] | Ductless Heat Pump | HP-9 | Mitsubishi | PUZ-A24NHA4 | 23.8 | MBH |  |  | Unknown | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | York | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 15 kW
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | York | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 15 kW
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | York | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 10 kW
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | York | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 10 kW
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | York | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 10 kW
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-6 | York | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 10 kW
14- 526453-1 [RTU] | Air Source Heat Pump (Packaged Rooftop) | RTU-7 | York | XP048C00B2C1AAA1A1 | 41 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 10 kW
18- 595441 | Gas-fired Packaged Rooftop HVAC | RTU-101 | Carrier | 48KC04 | 44 | MBH | 1200 | CFM | 82 | Thermal Efficiency (%) |  |  | 0.51 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 595441 | Gas-fired Packaged Rooftop HVAC | RTU-102 | Carrier | 48KC04 | 44 | MBH | 1200 | CFM | 82 | Thermal Efficiency (%) |  |  | 0.51 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 595441 | Gas-fired Packaged Rooftop HVAC | RTU-103 | Carrier | 48KC05 | 44 | MBH | 1600 | CFM | 82 | Thermal Efficiency (%) |  |  | 0.78 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 595441 | Gas-fired Packaged Rooftop HVAC | RTU-104 | Carrier | 48KC05 | 64.2 | MBH | 1600 | CFM | 82 | Thermal Efficiency (%) |  |  | 0.78 | BHP | Natural Gas | [5 empty] | N/A | N/A
14- 540112-1 [Corridors\Main Floor Areas] | Gas-fired Packaged Rooftop HVAC | RTU-1 | AAON | RQ-004 | 113 | MBH | 1600 | CFM | 81 | Thermal Efficiency (%) |  |  | 2 | Fan HP | Natural Gas | [5 empty] | N/A | N/A
14- 540112-1 [Misc.] | Ductless Heat Pump | CU-1 | Daikin | RX18NMVJU | 21600 | Btu/hr |  |  | 9 | HSPF | 3.6 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
14- 540112-1 [Misc.] | Ductless Heat Pump | CU-3 | Fujitsu | AOU30RLXB | 30000 | Btu/hr |  |  | 9 | HSPF | 3.14 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
14- 540112-1 [Misc.] | Ductless Heat Pump | CU-4 | Daikin | RX18NMJVU | 21600 | Btu/hr |  |  | 9 | HSPF | 3.6 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
14- 540112-1 [Misc.] | Ductless Heat Pump | CU-5 | Daikin | RX12NMJVU | 13500 | Btu/hr |  |  | 9 | HSPF | 3.8 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
14- 540112-1 [Misc.] | Ductless Heat Pump | CU-6 | Daikin | RX12NMJVU | 13500 | Btu/hr |  |  | 9 | HSPF | 3.8 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-N | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-NE | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-NW | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-S | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-SE | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-SW | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-A-W | Fujitsu | A0UA96TLCV | 103 | MBH |  |  | 3.72 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-B-E | Fujitsu | AQUA192TLCVG | 206 | MBH |  |  | 3.75 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-B-N | Fujitsu | AQUA192TLCVG | 206 | MBH |  |  | 3.75 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-B-NE | Fujitsu | AQUA192TLCVG | 206 | MBH |  |  | 3.75 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-B-S | Fujitsu | AQUA168TLCVG | 180 | MBH |  |  | 3.48 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-C-SW | Fujitsu | AQUA192TLCVG | 206 | MBH |  |  | 3.75 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-C-W | Fujitsu | AQUA144TLCVG | 154 | MBH |  |  | 3.44 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-D-E | Fujitsu | AQUA216TLCVG | 232 | MBH |  |  | 3.47 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 550027-2 | Variable Refrigerant Flow | VRF-D-W | Fujitsu | AQUA216TLCVG | 232 | MBH |  |  | 3.47 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 673795-2 | Variable Refrigerant Flow | ACU-1 | Mitsubishi | PURY-P288TSLMU-A | 217 | MBH |  |  | 3.38 | COP(47) | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
14- 673795-2 | Variable Refrigerant Flow | ACU-2 | Mitsubishi | PURY-P288TSLMU-A | 217 | MBH |  |  | 3.38 | COP(47) | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
14- 673795-2 | Variable Refrigerant Flow | ACU-3 | Mitsubishi | PUMY-P36NHMU | 37.2 | MBH |  |  | 3.14 | COP(47) | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
14- 587282-1 | Variable Refrigerant Flow | CU-1 | Daikin | REYQ216PBTJ | 231 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 587282-1 | Variable Refrigerant Flow | CU-2 | Daikin | REYQ192PBTJ | 206 | MBH |  |  | 3.4 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 587282-1 | Variable Refrigerant Flow | CU-3 | Daikin | REYQ216PBTJ | 231 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 611061-1 | Air Source Heat Pump AHU (split system) | HP-2B | Carrier | 25HHA436 | 36 | MBH | 1200 | CFM | 3.9 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Unknown | Unknown
14- 611061-1 | Air Source Heat Pump AHU (split system) | HP-3B | Carrier | 25HHA448 | 48 | MBH | 1600 | CFM | 3.9 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Unknown | Unknown
14- 611061-1 | Air Source Heat Pump AHU (split system) | HP-4B | Carrier | 25HHA448 | 48 | MBH | 1600 | CFM | 3.9 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Unknown | Unknown
14- 626014-1 | Ductless Heat Pump | CU-1 | Mitsubishi | SUZ-KA15NA | 18 | MBH |  |  | 9.6 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-10 | Mitsubishi | SUZ-KA12NA | 13.6 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-11 | Mitsubishi | SUZ-KA15NA | 18 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-12 | Mitsubishi | SUZ-KA18NA | 21.6 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-15 | Mitsubishi | PUZ-A18NHA4 | 19 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-16 | Mitsubishi | MXZ-3C24NA | 18 | MBH |  |  | 9.6 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-17 | Mitsubishi | MXZ-5C42NAHZ | 13.6 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-18 | Mitsubishi | PUZ-A12NHA4 | 18 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-19 | Mitsubishi | PUMY-P60NKMU | 21.6 | MBH |  |  | 10.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-4 | Mitsubishi | MUZ-GE09NA | 10.9 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-5 | Mitsubishi | PUZ-A24NHA4 | 48 | MBH |  |  | 10.6 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-6 | Mitsubishi | PUZ-A30NHA4 | 19 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-7 | Mitsubishi | PUZ-HA36NHA4 | 37 | MBH |  |  | 9.8 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-8 | Mitsubishi | PUZ-HA42NKA | 45 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 626014-1 | Ductless Heat Pump | CU-9 | Mitsubishi | SUZ-KA09NA | 10.9 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#1 | Lennox | LGH120H4BM-G | 144000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#10 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#11 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#12 | Lennox | LGH036H4EM-G | 84000 | Btu/hr | 1200 | CFM | 78 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#2 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#3 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#4 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#5 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#6 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#7 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#8 | Lennox | LGH060H4EM-G | 84000 | Btu/hr | 2000 | CFM | 78 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 634379-1 | Gas-fired Packaged Rooftop HVAC | HL#9 | Lennox | LGH092H4BM-G | 144000 | Btu/hr | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-21 | Trane | YHC036 | 48 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-22 | Trane | YHC036 | 48 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-23 | Trane | YHC036 | 48 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-24 | Trane | YHC120 | 84 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-25 | Trane | YHD150 | 122 | MBH | 5000 | CFM | 81 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-26 | Trane | YHD150 | 122 | MBH | 5000 | CFM | 81 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-27 | Trane | YHC036 | 48 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 662676-1 | Gas-fired Packaged Rooftop HVAC | AC-28 | Trane | YHC036 | 48 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.00.1 | Mitsubishi | PURY-P264YSKMU-A | 295 | MBH |  |  | 3.4 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.01.1 | Mitsubishi | PURY-P264YSKMU-A | 295 | MBH |  |  | 3.4 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.02.1 | Mitsubishi | PURY-P288YSKMU-A | 320 | MBH |  |  | 3.41 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.03.1 | Mitsubishi | PURY-P288YSKMU-A | 320 | MBH |  |  | 3.41 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.04.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.05.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.06.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.07.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.08.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R1.09.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.00.1 | Mitsubishi | PURY-P264YSKMU-A | 295 | MBH |  |  | 3.4 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.01.1 | Mitsubishi | PURY-P264YSKMU-A | 295 | MBH |  |  | 3.4 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.03.2 | Mitsubishi | PURY-P288YSKMU-A | 320 | MBH |  |  | 3.41 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.04.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.05.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.06.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.07.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.08.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R2.09.2 | Mitsubishi | PURY-P216YSKMU-A | 243 | MBH |  |  | 3.54 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.00.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.01.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.02.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.03.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.04.1 | Mitsubishi | PURY-P240YSKMU-A | 270 | MBH |  |  | 3.38 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.05.2 | Mitsubishi | PURY-P168YSKMU-A | 188 | MBH |  |  | 3.63 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.06.2 | Mitsubishi | PURY-P168YSKMU-A | 188 | MBH |  |  | 3.63 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.07.2 | Mitsubishi | PURY-P168YSKMU-A | 188 | MBH |  |  | 3.63 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.08.2 | Mitsubishi | PURY-P168YSKMU-A | 188 | MBH |  |  | 3.63 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 668269-1 | Variable Refrigerant Flow | R3.09.2 | Mitsubishi | PURY-P168YSKMU-A | 188 | MBH |  |  | 3.63 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 731874-1 [RTU] | Gas-fired Packaged Rooftop HVAC | RTU-1 | Daikin | MPSH15B | 284 | MBH | 6000 | CFM | 350 | Heating Input Capacity (MBH) |  |  | 5.75 | HP | Natural Gas | [5 empty] | N/A | N/A
14- 731874-1 [VRF] | Variable Refrigerant Flow | HP-1 | Daikin | REYQ168TYDN | 108.2 | MBH |  |  | 3.33 | COP(47) | 2.15 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
14- 731874-1 [VRF] | Variable Refrigerant Flow | HP-2 | Daikin | REYQ72TYDN | 59.1 | MBH |  |  | 3.82 | COP(47) | 2.63 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Unknown | Unknown | 200 | MBH | 6500 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Unknown | Unknown | 240 | MBH | 3700 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-12 | Unknown | Unknown | 105 | MBH | 1200 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-13 | Unknown | Unknown | 105 | MBH | 1200 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-14 | Unknown | Unknown | 480 | MBH | 9000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-15 | Unknown | Unknown | 480 | MBH | 9000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-16 | Unknown | Unknown | 480 | MBH | 9000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-17 | Unknown | Unknown | 480 | MBH | 6500 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-18 | Unknown | Unknown | 130 | MBH | 4800 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-19 | Unknown | Unknown | 280 | MBH | 8000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Unknown | Unknown | 240 | MBH | 3700 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-20 | Unknown | Unknown | 280 | MBH | 8000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-21 | Unknown | Unknown | 130 | MBH | 4500 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-22 | Unknown | Unknown | 480 | MBH | 9000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-23 | Unknown | Unknown | 480 | MBH | 9000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-24 | Unknown | Unknown | 105 | MBH | 1200 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-25 | Unknown | Unknown | 240 | MBH | 3700 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-26 | Unknown | Unknown | 240 | MBH | 3700 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-27 | Unknown | Unknown | 240 | MBH | 3700 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-28 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-29 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-30 | Unknown | Unknown | 400 | MBH | 6000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-31 | Unknown | Unknown | 400 | MBH | 6000 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-32 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Unknown | Unknown | 150 | MBH | 1650 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Unknown | Unknown | 100 | MBH | 1200 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 411092-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Unknown | Unknown | 100 | MBH | 1200 | CFM | 80 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 419460-1 | Variable Refrigerant Flow | CU-1a | Mitsubishi | PURY-192TSLMU | 92 | MBH |  |  | 3.53 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 419460-1 | Variable Refrigerant Flow | CU-1b | Mitsubishi | PURY-192TSLMU | 92 | MBH |  |  | 3.53 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 419460-1 | Variable Refrigerant Flow | CU-2 | Mitsubishi | MXZ-8C48NA | 54 | MBH |  |  | 3.46 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 419460-1 | Variable Refrigerant Flow | CU-3 | Mitsubishi | MXZ-8C48NA | 54 | MBH |  |  | 3.46 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 425673-1 | Variable Refrigerant Flow | HP-1 | MITSUBISHI | PURY | 135 | MBH |  |  | 3.4 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 425673-1 | Variable Refrigerant Flow | HP-2 | MITSUBISHI | PURY | 80 | MBH |  |  | 3.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48KC06 | 56000 | Btu/hr | 2000 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Carrier | 48TC17 | 178000 | Btu/hr | 6000 | CFM | 80.1 | Thermal Efficiency (%) |  |  | 3.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Carrier | 48TC17 | 178000 | Btu/hr | 6000 | CFM | 80.1 | Thermal Efficiency (%) |  |  | 3.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-12 | Carrier | 48KC06 | 56000 | Btu/hr | 2000 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-13 | Carrier | 48KC05 | 56000 | Btu/hr | 1600 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-14 | Carrier | 48TC07 | 56000 | Btu/hr | 2400 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-15 | Carrier | 48KC06 | 56000 | Btu/hr | 2000 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-16 | Carrier | 48KC06 | 56000 | Btu/hr | 2000 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48TC09 | 148000 | Btu/hr | 3400 | CFM | 82.2 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48TC24 | 178000 | Btu/hr | 8000 | CFM | 80.9 | Thermal Efficiency (%) |  |  | 8.3 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Carrier | 48KC04 | 56000 | Btu/hr | 1200 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Carrier | 48KC04 | 56000 | Btu/hr | 1200 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Carrier | 48TC08 | 103000 | Btu/hr | 3000 | CFM | 82.4 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Carrier | 48KC05 | 56000 | Btu/hr | 1600 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Carrier | 48TC07 | 56000 | Btu/hr | 24000 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 427602-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Carrier | 48KC06 | 56000 | Btu/hr | 2000 | CFM | 77.8 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 458201-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | AAON | RQ | 27 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.25 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 458201-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | AAON | RQ | 34 | MBH | 1600 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 458201-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | AAON | RN | 198 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 458201-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | AAON | RN | 198 | MBH | 5400 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 458201-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | AAON | RN | 141 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-2A | Daikin | REYQ168TTJU | 352000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-2B | Daikin | N/A | 150000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-3A | Daikin | N/A | 176000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-3B | Daikin | N/A | 150000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-4A | Daikin | N/A | 150000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-4B | Daikin | N/A | 150000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-5A | Daikin | N/A | 150000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-5B | Daikin | N/A | 150000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-6A | Daikin | N/A | 176000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-6B | Daikin | N/A | 176000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 464466-1 | Variable Refrigerant Flow | HRU-A1 | Daikin | REYQ264TTJU | 162793 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | YORK | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | YORK | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | YORK | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | YORK | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | YORK | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-6 | YORK | XP060C00B2C1AAA1A1 | 56.5 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 472299-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-7 | YORK | XP048C00B2C1AAA1A1 | 41 | MBH |  |  | 7.7 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
15- 527020-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Carrier | 48HCFA06 | 117 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 580950-1 | Variable Refrigerant Flow | ACU-R-X-1 | LG | ARUB096DTE4 | 96000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 580950-1 | Variable Refrigerant Flow | ACU-R-X-2 | LG | ARUB096DTE4 | 240000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 580950-1 | Variable Refrigerant Flow | ACU-R-X-3 | LG | ARUB216DTE4 | 216000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 580950-1 | Variable Refrigerant Flow | ACU-R-X-4 | LG | ARUB264DTE4 | 264000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 580950-1 | Variable Refrigerant Flow | ACU-R-X-5 | LG | ARUB360DTE4 | 360000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 580950-1 | Variable Refrigerant Flow | ACU-R-X-6 | LG | ARUB168DTE4 | 168000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 589031-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YHD180F3RHA | 232.8 | MBH | 6000 | CFM | Unknown |  |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 589031-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YHD300F3RHA | 265.6 | MBH | 9500 | CFM | Unknown |  |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
15- 602446-1 | Variable Refrigerant Flow | CU-1 | Mitsubishi | PURY-HP192TSKMU-A-H | 215000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 602446-1 | Variable Refrigerant Flow | CU-2 | Mitsubishi | PURY-HP192TSKMU-A-H | 215000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 602446-1 | Variable Refrigerant Flow | CU-3 | Mitsubishi | PURY-HP192TSKMU-A-H | 215000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 602446-1 | Variable Refrigerant Flow | CU-4 | Mitsubishi | PUZ-A18NHA3 | 19000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 602446-1 | Variable Refrigerant Flow | CU-5 | Mitsubishi | PURY-HP96TSKMU-A-H | 108000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
03- 779006-1 | Variable Refrigerant Flow | HP-1 | Daikin | REYQ120TYDN | 105 | MBH |  |  | 3.5 | COP(47) | 2.3 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-1 | LG | ARUN038GSS4 | 42 | MBH |  |  | 8.6 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-2 | LG | LUU247 | 27 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-3 | LG | LUU187HV | 22 | MBH |  |  | 10.1 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-4 | LG | LSU240HEV1 | 24.2 | MBH |  |  | 9 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-5 | LG | LSU180HSV | 22 | MBH |  |  | 9.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-6 | LG | LSU180HSV | 22 | MBH |  |  | 9.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 692220-1 | Ductless Heat Pump | HP-7 | LG | LSU180HSV | 22 | MBH |  |  | 9.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 700290-1 | Gas-fired Packaged Rooftop HVAC | RT-1 | Carrier | 48TCD012 | 184 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 700290-1 | Gas-fired Packaged Rooftop HVAC | RT-2 | Carrier | 48TCD014 | 184 | MBH | 4800 | CFM | 80 | Thermal Efficiency (%) |  |  | 4.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 700290-1 | Gas-fired Packaged Rooftop HVAC | RT-3 | Carrier | 48TCD06 | 93 | MBH | 1950 | CFM | 80 | Thermal Efficiency (%) |  |  | 2.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 700290-1 | Gas-fired Packaged Rooftop HVAC | RT-4 | Carrier | 48TCD05 | 115 | MBH | 1600 | CFM | 93 | Thermal Efficiency (%) |  |  | 1.2 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 400924-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | AAON | RN050 | 432 | MBH | 19400 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
16- 400924-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | AAON | RN050 | 432 | MBH | 19400 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
16- 400924-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | AAON | RN050 | 432 | MBH | 19400 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
16- 400924-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | AAON | RN026 | 432 | MBH | 10650 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
16- 403736-1 | Variable Refrigerant Flow | HP-1 | Trane | TUHYP072AN40A(N/B) | 80000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-10 | Carrier | 59SC06010 | 58 | MBH | 1200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-11 | Carrier | 59SC06010 | 58 | MBH | 1200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-12 | Carrier | 59SC06010 | 58 | MBH | 1200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-13 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-14 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-15 | Carrier | 59SC08016 | 78 | MBH | 1600 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-16 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-3 | Carrier | 59SC08016 | 78 | MBH | 1400 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-4 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-5 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-6 | Carrier | 59SC06010 | 58 | MBH | 1200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-7 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-8 | Carrier | 59SC08016 | 78 | MBH | 1600 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 404663-1 | Gas-fired indoor air handling unit | F-9 | Carrier | 59SC12020 | 117 | MBH | 1800 | CFM | 95 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Unknown | Unknown | 360 | MBH | 8000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Unknown | Unknown | 260 | MBH | 8000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Unknown | Unknown | 360 | MBH | 8000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Unknown | Unknown | 360 | MBH | 7000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Unknown | Unknown | 360 | MBH | 7000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Unknown | Unknown | 130 | MBH | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Unknown | Unknown | 480 | MBH | 10000 | CFM | 80 | Thermal Efficiency (%) |  |  | 10 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Unknown | Unknown | 480 | MBH | 10000 | CFM | 80 | Thermal Efficiency (%) |  |  | 10 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Unknown | Unknown | 360 | MBH | 8000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 412293-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Unknown | Unknown | 360 | MBH | 8000 | CFM | 80 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 423218-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Daikin | MHS007B | 87 | MBH | 2600 | CFM | 3.4 | COP(47) |  |  | 2 | Fan HP | Electric | [5 empty] | Yes | 10.8 kW
16- 423218-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Daikin | MHSH03B | 34.4 | MBH | 1200 | CFM | 7.7 | HSPF |  |  | 0.75 | Fan HP | Electric | [5 empty] | Yes | 7.2 kW
16- 423218-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Daikin | MHSH03B | 34.4 | MBH | 1200 | CFM | 7.7 | HSPF |  |  | 0.75 | Fan HP | Electric | [5 empty] | Yes | 7.2 kW
16- 423218-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Daikin | MHSH03B | 34.4 | MBH | 1050 | CFM | 7.7 | HSPF |  |  | 0.75 | Fan HP | Electric | [5 empty] | Yes | 7.2 kW
16- 423218-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | Daikin | MHSH05B | 34.4 | MBH | 1900 | CFM | 7.7 | HSPF |  |  | 1 | Fan HP | Electric | [5 empty] | Yes | 7.2 kW
16- 423218-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-6 | Daikin | MHSH03B | 34.4 | MBH | 1200 | CFM | 7.7 | HSPF |  |  | 0.75 | Fan HP | Electric | [5 empty] | Yes | 7.2 kW
16- 427879-1 | Gas-fired Packaged Rooftop HVAC | AHU-A01 | Carrier | 39M | 240 | MBH | 5440 | CFM | 80 | Thermal Efficiency (%) |  |  | 13 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 427879-1 | Gas-fired Packaged Rooftop HVAC | AHU-A02 | Carrier | 39M | 240 | MBH | 5300 | CFM | 80 | Thermal Efficiency (%) |  |  | 13 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 427879-1 | Gas-fired Packaged Rooftop HVAC | AHU-A03 | Carrier | 39M | 150 | MBH | 2040 | CFM | 80 | Thermal Efficiency (%) |  |  | 4.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 427879-1 | Gas-fired Packaged Rooftop HVAC | AHU-A04 | Carrier | 39M | 150 | MBH | 1630 | CFM | 80 | Thermal Efficiency (%) |  |  | 2.25 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 438381-1 | Gas-fired Packaged Rooftop HVAC | HVAC-1 | Trane | YSH240F3RLA | 203000 | Btu/hr | 8000 | CFM | 80 | AFUE |  |  | 0.1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 438381-1 | Gas-fired Packaged Rooftop HVAC | HVAC-2 | Trane | YSH240F3RLA | 203000 | Btu/hr | 8000 | CFM | 80 | AFUE |  |  | 0.1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 490400-1 | Variable Refrigerant Flow | HP-1 | Mitsubishi | PURY-HP96TKMU-A-H | 108000 | Btu/hr |  |  | 3.47 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 730160-1 | Variable Refrigerant Flow | HP 1N | Daikin | REYQ288TYDN | 198 | MBH |  |  | 3.26 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 730160-1 | Variable Refrigerant Flow | HP 1S | Daikin | REYQ336TYDN | 205.1 | MBH |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 730160-1 | Variable Refrigerant Flow | HP 2 | Daikin | REYQ408TYDN | 272 | MBH |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
14- 730160-1 | Variable Refrigerant Flow | HP 3 | Daikin | REYQ456TYDN | 303 | MBH |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | Gas-fired indoor air handling unit | DF-1 | Reznor | SC | 280 | MBH | 7200 | CFM | 80 | Thermal Efficiency (%) |  |  | 12.5 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | Gas-fired indoor air handling unit | DF-2 | Reznor | SC | 280 | MBH | 5175 | CFM | 80 | Thermal Efficiency (%) |  |  | 8 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | Gas-fired indoor air handling unit | DF-3 | Reznor | SC | 320 | MBH | 7965 | CFM | 80 | Thermal Efficiency (%) |  |  | 15 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | Gas-fired indoor air handling unit | DF-4 | Reznor | SC | 240 | MBH | 5660 | CFM | 80 | Thermal Efficiency (%) |  |  | 10 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 419203-1 [Additional Areas] | Variable Refrigerant Flow | OHP-1 | Daikin | REYQ360PBTJ | 385000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 419203-1 [Additional Areas] | Variable Refrigerant Flow | OHP-2 | Daikin | REYQ360PBTJ | 385000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 419203-1 [Additional Areas] | Variable Refrigerant Flow | OHP-3 | Daikin | REYQ360PBTJ | 385000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
15- 419203-1 [Additional Areas] | Variable Refrigerant Flow | OHP-4 | Daikin | REYQ360PBTJ | 385000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
16- 514976-1 | Variable Refrigerant Flow | HP1 | Daikin | REYQ168TTJU | 188000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 514976-1 | Variable Refrigerant Flow | HP3 | Daikin | RMXS48LVJU | 54000 | Btu/hr |  |  | 11.3 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 514976-1 | Variable Refrigerant Flow | HP4 | Daikin | REYQ96TTJU | 108000 | Btu/hr |  |  | 4.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 514976-1 | Variable Refrigerant Flow | HP5 | Daikin | RXN12NMVJU | 12000 | Btu/hr |  |  | 8.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 536718-1 | Variable Refrigerant Flow | VRF-A | Daikin | REYQ168TATJU | 108.5 | MBH |  |  | 3.7 | COP(47) | 2.22 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
16- 536718-1 | Variable Refrigerant Flow | VRF-B | Daikin | REYQ168TATJU | 108.5 | MBH |  |  | 3.7 | COP(47) | 2.22 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
16- 536718-1 | Variable Refrigerant Flow | VRF-C | Daikin | REYQ96TATJU | 78.6 | MBH |  |  | 4.25 | COP(47) | 2.52 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-1 | LG | ARUM336 | 378 | MBH |  |  | 3.24 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-10 | LG | ARUB384 | 432 | MBH |  |  | 3.22 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-11 | LG | ARUM336 | 378 | MBH |  |  | 3.24 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-12 | LG | ARUM096 | 108 | MBH |  |  | 3.48 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-13 | LG | ARUN168 | 189 | MBH |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-14 | LG | ARUN168 | 189 | MBH |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-2 | LG | ARUB384 | 432 | MBH |  |  | 3.22 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-3 | LG | ARUM096 | 108 | MBH |  |  | 3.48 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-4 | LG | ARUM096 | 108 | MBH |  |  | 3.48 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-5 | LG | ARUB120 | 135 | MBH |  |  | 3.46 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-6 | LG | ARUM096 | 108 | MBH |  |  | 3.48 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-7 | LG | ARUM096 | 108 | MBH |  |  | 3.48 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-8 | LG | ARUB120 | 135 | MBH |  |  | 3.46 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 537171-1 | Variable Refrigerant Flow | CU R-9 | LG | ARUB384 | 432 | MBH |  |  | 3.22 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 558605-2 | Air Source Heat Pump AHU (split system) | HP-C100-1 | LG | ARUN048GSS4 | 54000 | Btu/hr | 1500 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
16- 558605-2 | Air Source Heat Pump AHU (split system) | HP-C100-2 | LG | ARUN048GSS4 | 54000 | Btu/hr | 1500 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
16- 558605-2 | Air Source Heat Pump AHU (split system) | HP-C100-3 | LG | ARUN048GSS4 | 54000 | Btu/hr | 1500 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
16- 572659-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48TC08 | 98 | MBH | 3000 | CFM | 120 | Heating Input Capacity (MBH) |  |  | 1.95 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 577162-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48TCEA05 | 82 | MBH | 1600 | CFM | 0.81 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
16- 577162-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48TCEA05 | 82 | MBH | 1600 | CFM | 0.81 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
16- 577162-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48TCEA05 | 82 | MBH | 1600 | CFM | 0.81 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
16- 577162-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Carrier | 48TCEA05 | 82 | MBH | 1600 | CFM | 0.81 | AFUE |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
16- 607207-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48FC06 | 88 | MBH | 2000 | CFM | 110 | Heating Input Capacity (MBH) |  |  | 1.21 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 607207-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48FC06 | 88 | MBH | 2000 | CFM | 110 | Heating Input Capacity (MBH) |  |  | 1.21 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 607207-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48HC11 | 148 | MBH | 4000 | CFM | 180 | Heating Input Capacity (MBH) |  |  | 2.41 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 607207-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Carrier | 48FC04 | 93 | MBH | 1200 | CFM | 110 | Heating Input Capacity (MBH) |  |  | 0.48 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 615057-1 | Air Source Heat Pump AHU (split system) | HP-1-2 | Carrier | 25HCD336A006 | 33.76 | MBH | 1350 | CFM | 8 | HSPF | Unknown |  |  |  | Electric | [5 empty] | No | N/A
16- 615057-1 | Air Source Heat Pump AHU (split system) | HP-1-3 | Carrier | 25HCD336A006 | 33.04 | MBH | 1140 | CFM | 8 | HSPF | Unknown |  |  |  | Electric | [5 empty] | No | N/A
16- 615057-1 | Air Source Heat Pump AHU (split system) | HP-1-4 | Carrier | 25HCD336A006 | 21.94 | MBH | 780 | CFM | 8.2 | HSPF | Unknown |  |  |  | Electric | [5 empty] | No | N/A
16- 615057-1 | Air Source Heat Pump AHU (split system) | HP-2-1 | Carrier | 25HCD336A006 | 57.42 | MBH | 1720 | CFM | 7.7 | HSPF | Unknown |  |  |  | Electric | [5 empty] | No | N/A
16- 621440-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Daikin | DSG0360454BXXX | 36.8 | MBH | 1200 | CFM | 46 | Heating Input Capacity (MBH) |  |  | Unknown | N/A | Natural Gas | [5 empty] | N/A | N/A
16- 621440-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Daikin | DSG0490904BXXX | 74 | MBH | 1600 | CFM | 92 | Heating Input Capacity (MBH) |  |  | Unknown | N/A | Natural Gas | [5 empty] | N/A | N/A
16- 640402-1 | Ductless Heat Pump | HP-1 | Mitsubishi | PUZ-A12NKA7-BS | 14 | MBH |  |  | 10.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 640402-1 | Ductless Heat Pump | HP-12 | Mitsubishi | PUZ-A12NKA7-BS | 11.1 | MBH |  |  | 10.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 640402-1 | Ductless Heat Pump | HP-18 | Mitsubishi | MUZ-GL18NA-U1 | 18.2 | MBH |  |  | 11.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 640402-1 | Ductless Heat Pump | HP-3 | Mitsubishi | MUZ-GL18NA-U1 | 18.2 | MBH |  |  | 11.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 640402-1 | Ductless Heat Pump | HP-9 | Mitsubishi | MUZ-HM09NA2-U8 | 7.2 | MBH |  |  | 8.5 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48HC-09 | 184 | MBH | 3400 | CFM | 82 | Thermal Efficiency (%) |  |  | 1.66 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Carrier | 48HC-12 | 184 | MBH | 4000 | CFM | 82.1 | Thermal Efficiency (%) |  |  | 2.16 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Carrier | 48HC-08 | 103 | MBH | 3160 | CFM | 82.4 | Thermal Efficiency (%) |  |  | 1.09 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-12 | Carrier | 48HC-20 | 324 | MBH | 7000 | CFM | 81 | Thermal Efficiency (%) |  |  | 5.3 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-13 | Carrier | 48HC-08 | 103 | MBH | 2650 | CFM | 82.4 | Thermal Efficiency (%) |  |  | 1.09 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-14 | Carrier | 48HC-17 | 324 | MBH | 6760 | CFM | 81 | Thermal Efficiency (%) |  |  | 5.3 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48HC-11 | 195 | MBH | 6000 | CFM | 81 | Thermal Efficiency (%) |  |  | 2.05 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-3A | Carrier | 48HC-08 | 148 | MBH | 3000 | CFM | 82.2 | Thermal Efficiency (%) |  |  | 1.09 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-3B | Carrier | 48HC-08 | 148 | MBH | 3400 | CFM | 82.2 | Thermal Efficiency (%) |  |  | 1.66 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-4A | Carrier | 48HC-08 | 148 | MBH | 3000 | CFM | 82.2 | Thermal Efficiency (%) |  |  | 1.09 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-4B | Carrier | 48HC-12 | 184 | MBH | 4000 | CFM | 82 | Thermal Efficiency (%) |  |  | 2.16 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-4C | Carrier | 48HC-14 | 195 | MBH | 6000 | CFM | 81.25 | Thermal Efficiency (%) |  |  | 2.05 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-5A | Carrier | 48HC-09 | 148 | MBH | 3400 | CFM | 82.2 | Thermal Efficiency (%) |  |  | 1.66 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-5B | Carrier | 48HC-09 | 148 | MBH | 3400 | CFM | 82.2 | Thermal Efficiency (%) |  |  | 1.66 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Carrier | 48HC-09 | 184 | MBH | 3400 | CFM | 82.1 | Thermal Efficiency (%) |  |  | 1.66 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Carrier | 48HC-14 | 195 | MBH | 6000 | CFM | 81.25 | Thermal Efficiency (%) |  |  | 2.05 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Carrier | 48HC-14 | 195 | MBH | 6000 | CFM | 81.25 | Thermal Efficiency (%) |  |  | 2.05 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 573278-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Carrier | 48HC-09 | 184 | MBH | 3400 | CFM | 82.1 | Thermal Efficiency (%) |  |  | 1.66 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 657491-1 | Variable Refrigerant Flow | MS1 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 7.9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 657491-1 | Variable Refrigerant Flow | MS2 | Daikin | FXYMQ48PVJU | 53 | MBH |  |  | 9.1 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 662436-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YSC036G3 | 49.2 | MBH | 1200 | CFM | 0.82 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | No | N/A
16- 662436-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YSC102F3 | 96 | MBH | 3400 | CFM | 0.8 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | No | N/A
16- 662436-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YSC102F3 | 96 | MBH | 3400 | CFM | 0.8 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | No | N/A
16- 662436-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | YSC102F3 | 96 | MBH | 3000 | CFM | 0.8 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | No | N/A
16- 680124-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Johnson Controls | J25ZIN30P4B5BCA2C1 | 240 | MBH | 10000 | CFM | 300 | Heating Input Capacity (MBH) |  |  | 9.14 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 680124-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Johnson Controls | J25ZIN30P4B5BCA2C1 | 240 | MBH | 10000 | CFM | 300 | Heating Input Capacity (MBH) |  |  | 9.14 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 680124-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Johnson Controls | J25ZIN30P4B5BCA2C1 | 240 | MBH | 10000 | CFM | 300 | Heating Input Capacity (MBH) |  |  | 9.14 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 680124-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Johnson Controls | JA3IN06B4B5BCA2A1 | 49 | MBH | 900 | CFM | 60 | Heating Input Capacity (MBH) |  |  | 0.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 680124-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Johnson Controls | JZ4ZIN06B4B5BCA2AI | 49 | MBH | 900 | CFM | 60 | Heating Input Capacity (MBH) |  |  | 0.98 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 680124-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Johnson Controls | J12ZIN18R4B5BCA2AI | 144 | MBH | 5000 | CFM | 180 | Heating Input Capacity (MBH) |  |  | 4.74 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 688717-1 [RTU] | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48KCEA06 | 73 | MBH | 2000 | CFM | 82 | Thermal Efficiency (%) |  |  | Unknown | N/A | Natural Gas | [5 empty] | N/A | N/A
16- 688717-1 [RTU] | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48KCEA06 | 73 | MBH | 2000 | CFM | 82 | Thermal Efficiency (%) |  |  | Unknown | N/A | Natural Gas | [5 empty] | N/A | N/A
16- 688717-1 [RTU] | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48KCEA06 | 73 | MBH | 2000 | CFM | 82 | Thermal Efficiency (%) |  |  | Unknown | N/A | Natural Gas | [5 empty] | N/A | N/A
16- 688717-1 [VRF] | Variable Refrigerant Flow | ODU-1 | LG | ARUM168BTE5 | 154.6 | MBH |  |  | 3.2 | COP(47) | 2.38 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
16- 706094-1 | Variable Refrigerant Flow | ACCU-701 | LG | ARUM336BTE5 | 378000 | Btu/hr |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 706094-1 | Variable Refrigerant Flow | ACCU-702 | LG | ARUM312BTE5 | 351000 | Btu/hr |  |  | 3.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 706094-1 | Variable Refrigerant Flow | ACCU-703 | LG | ARUM408BTE5 | 459000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 706094-1 | Variable Refrigerant Flow | ACCU-704 | LG | ARUM288BTE5 | 324000 | Btu/hr |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 706094-1 | Variable Refrigerant Flow | ACCU-705 | LG | ARUM336BTE5 | 378000 | Btu/hr |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 720532-1 | Gas-fired Packaged Rooftop HVAC | AC#1 | Lennox | LRP16GE | 384 | MBH | 8000 | CFM | 80 | AFUE |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 720532-1 | Gas-fired Packaged Rooftop HVAC | AC#2 | Lennox | LRP16GE | 192 | MBH | 4000 | CFM | 80 | AFUE |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 720532-1 | Gas-fired Packaged Rooftop HVAC | AC#3 | Lennox | LRP14GE | 192 | MBH | 5000 | CFM | 80 | AFUE |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 720532-1 | Gas-fired Packaged Rooftop HVAC | AC#4 | Lennox | LRP14GE | 120 | MBH | 1800 | CFM | 80 | AFUE |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-1 | Mitsubishi | PUMY-P48NKMU1 | 43 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-10 | Mitsubishi | PUZ-A36NHA6 | 30 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-11 | Mitsubishi | PUMY-P48NKMU1 | 43 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-12 | Mitsubishi | PUZ-A36NHA6 | 30 | MBH |  |  | 2.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-13 | Mitsubishi | PUMY-P48NKMU1 | 43 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-14 | Mitsubishi | PUMY-P48NKMU1 | 43 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-15 | Mitsubishi | MXZ-4C24NA | 20.8 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-16 | Mitsubishi | MXZ-3C30NA | 25.6 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-17 | Mitsubishi | PUZ-A36NHA6 | 30 | MBH |  |  | 2.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-18 | Mitsubishi | PUZ-A30NHA6 | 25.6 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-19 | Mitsubishi | MXZ-4C24NA | 20.8 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-2 | Mitsubishi | PUZ-A36NHA6 | 30 | MBH |  |  | 2.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-20 | Mitsubishi | MXZ-4C24NA | 25.6 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-21 | Mitsubishi | PUZ-A36NHA6 | 30 | MBH |  |  | 2.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-22 | Mitsubishi | MXZ-4C24NA | 20.8 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-3 | Mitsubishi | PUMY-P36NKMU1 | 34 | MBH |  |  | 3.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-4 | Mitsubishi | PUMY-P48NKMU1 | 43 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-5 | Mitsubishi | PUMY-P36NKMU1 | 27 | MBH |  |  | 3.6 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-6 | Mitsubishi | PUZ-A30NHA6 | 25.6 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-7 | Mitsubishi | PUMY-P48NKMU1 | 43 | MBH |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-8 | Mitsubishi | PUZ-A24NHA6 | 20.8 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
16- 727455-1 | Ductless Heat Pump | HP-9 | Mitsubishi | PUZ-A30NHA6 | 25.6 | MBH |  |  | 2.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-1 | Carrier | 59TP6 120-20 | 117 | MBH | 2115 | CFM | 96 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-2 | Carrier | 59TP6 60-14 | 58 | MBH | 1425 | CFM | 96 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-3 | Carrier | 59TP6 100-20 | 97 | MBH | 2005 | CFM | 96 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-4 | Carrier | 59TP6 60-12 | 58 | MBH | 1175 | CFM | 96 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-5 | Carrier | 59TP6 100-20 | 97 | MBH | 2000 | CFM | 96 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-6 | Carrier | 59TP6 80-20 | 78 | MBH | 1980 | CFM | 96 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | Gas-fired indoor air handling unit | FN-7 | Carrier | 59TP6 120-20 | 117 | MBH | 2000 | CFM | 96 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-1 | Daikin | RXYMQ48PVJU | 54 | MBH |  |  | 8.8 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-2 | Daikin | RXYMQ48PVJU | 54 | MBH |  |  | 8.8 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-3 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 8.4 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-4 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 8.4 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-5 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 8.4 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-6 | Daikin | RXYMQ48PVJU | 54 | MBH |  |  | 8.8 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-7 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 8.4 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-8 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 8.4 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
15- 640275-1 [Residences] | Variable Refrigerant Flow | HP-9 | Daikin | RXYMQ36PVJU | 42 | MBH |  |  | 8.4 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Daikin | MPSH03C | 64.8 | MBH | 1100 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Daikin | MPSH04C | 64.8 | MBH | 1300 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Daikin | MPSH05C | 81 | MBH | 1600 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Daikin | MPSH03C | 64.8 | MBH | 1100 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Daikin | MPSH03C | 64.8 | MBH | 1100 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Daikin | MPSH03C | 64.8 | MBH | 1100 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 429395-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Daikin | MPSH05C | 81 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 719739-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YHC120E3RHA | 200 | MBH | 3850 | CFM | 0.8 | Thermal Efficiency (%) |  |  | 2.75 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 719739-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YHD180F3RHA | 284 | MBH | 6000 | CFM | 0.81 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 719739-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YHD180F3RHA | 284 | MBH | 6000 | CFM | 0.81 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 719739-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | RRU241E3DFA | 651 | MBH | 6000 | CFM | 1 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 719739-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Trane | YHD180F3RHA | 284 | MBH | 6000 | CFM | 0.81 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-1 | Carrier | 25HBC324 | 30000 | Btu/hr | 800 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-10 | Carrier | 25HBC336 | 48000 | Btu/hr | 1200 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-11 | Carrier | 25HBC336 | 48000 | Btu/hr | 1200 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-12 | Carrier | 25HBC360 | 72000 | Btu/hr | 2000 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-13 | Carrier | 25HBC348 | 60000 | Btu/hr | 1600 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-2 | Carrier | 25HBC336 | 48000 | Btu/hr | 1200 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-3 | Carrier | 25HBC336 | 48000 | Btu/hr | 1200 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-4 | Carrier | 25HBC336 | 48000 | Btu/hr | 1600 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-6 | Carrier | 25HBC336 | 48000 | Btu/hr | 1200 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-7 | Carrier | 25HBC360 | 72000 | Btu/hr | 2000 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-8 | Carrier | 25HBC360 | 72000 | Btu/hr | 2000 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 1-9 | Carrier | 25HBC348 | 60000 | Btu/hr | 1600 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP 6-1 | Carrier | 25HBC324 | 30000 | Btu/hr | 800 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 521675-1 | Air Source Heat Pump AHU (split system) | HP P1-1 | Carrier | 25HHA424 | 30000 | Btu/hr | 800 | CFM | Unknown | [5 empty] | Electric | [5 empty] | No | N/A
17- 571695-2 | Variable Refrigerant Flow | MCU-1 | Mitsubishi | PURY-P312TSLMU-A | 350000 | Btu/hr |  |  | 3.27 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 571695-2 | Variable Refrigerant Flow | MCU-2 | Mitsubishi | PURY-P144TSLMU-A | 160000 | Btu/hr |  |  | 4.07 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 571695-2 | Variable Refrigerant Flow | MCU-3 | Mitsubishi | PURY-P192TSKMU-A | 215000 | Btu/hr |  |  | 3.47 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-01 | Daikin | REYQ288TAYDU | 192000 | Btu/hr |  |  | 3.2 | COP(47) | 2.15 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-02 | Daikin | REYQ336TAYDU | 336000 | Btu/hr |  |  | 3.2 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-03 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 3.27 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-04 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 3.27 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-05 | Daikin | REYQ432TAYDU | 432000 | Btu/hr |  |  | 3.2 | COP(47) | 2.06 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-06 | Daikin | REYQ432TAYDU | 432000 | Btu/hr |  |  | 3.2 | COP(47) | 2.06 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-07 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 3.27 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-08 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 3.27 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-09 | Daikin | REYQ456TAYDU | 456000 | Btu/hr |  |  | 3.2 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 584823-1 | Variable Refrigerant Flow | VRV-4-10 | Daikin | REYQ456TAYDU | 454286 | Btu/hr |  |  | 3.2 | COP(47) | 2.05 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 594224-1 | Air Source Heat Pump AHU (split system) | HP-1 | Bard | W36HA | 32000 | Btu/hr | 1100 | CFM | 3 | COP(47) |  |  |  |  | Electric | [5 empty] | No | N/A
17- 607886-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YHC102 | 105.5 | MBH | 3935 | CFM | 131.9 | Heating Input Capacity (MBH) |  |  | 3.8 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 607886-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YHC102 | 106.3 | MBH | 3440 | CFM | 132.9 | Heating Input Capacity (MBH) |  |  | 3.8 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 607886-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YHC036 | 44.3 | MBH | 1090 | CFM | 55.4 | Heating Input Capacity (MBH) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 607886-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | YHC036 | 42.9 | MBH | 1330 | CFM | 53.7 | Heating Input Capacity (MBH) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-1 | Lennox | TPA042 | 41.5 | MBH |  |  | 3.44 | COP(47) | 8 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-2 | Lennox | TPA042 | 41.5 | MBH |  |  | 3.44 | COP(47) | 8 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-3 | Lennox | TPA036 | 33.6 | MBH |  |  | 3.6 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-4 | Lennox | TPA036 | 33.6 | MBH |  |  | 3.6 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-5 | Lennox | TPA042 | 41.5 | MBH |  |  | 3.44 | COP(47) | 8 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-6 | Lennox | TPA042 | 41.5 | MBH |  |  | 3.44 | COP(47) | 8 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-7 | Lennox | TPA048 | 46 | MBH |  |  | 3.6 | COP(47) | 8.7 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 634478-1 | Ductless Heat Pump | HP-8 | Lennox | XP14018 | 17.7 | MBH |  |  | 3.84 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | N/A | N/A
17- 635582-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | TCD180B4L0OC | 250 | MBH | 5300 | CFM | 81 | AFUE |  |  | 81 | Watts | Natural Gas | [5 empty] | N/A | N/A
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWR5036H1 | 36 | MBH | 1070 | CFM | 3.6 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Yes | 7.2 kW
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWR5048H1 | 47 | MBH | 1650 | CFM | 3.6 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Yes | 10.8 kW
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWR5024H1 | 23 | MBH | 765 | CFM | 3.6 | COP(47) | 8.2 | HSPF |  |  | Electric | [5 empty] | Yes | 5.7 kW
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWR5048H1 | 47 | MBH | 1745 | CFM | 3.6 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Yes | 10.8 kW
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-5 | Trane | 4TWR5024H1 | 23 | MBH | 700 | CFM | 3.6 | COP(47) | 8.2 | HSPF |  |  | Electric | [5 empty] | Yes | 5.7 kW
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-6 | Trane | 4TWR5030H1 | 29 | MBH | 1000 | CFM | 3.9 | COP(47) | 9.5 | HSPF |  |  | Electric | [5 empty] | Yes | 5.7 kW
17- 636076-1 | Air Source Heat Pump AHU (split system) | HP-7 | Trane | 4TWR5048H1 | 47 | MBH | 1700 | CFM | 3.6 | COP(47) | 8.5 | HSPF |  |  | Electric | [5 empty] | Yes | 10.8 kW
17- 636076-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Trane | 4WCY5024A1000A | 22.4 | MBH | 700 | CFM | 8.3 | HSPF |  |  | 0.5 | HP | Electric | [5 empty] | Yes | 7.5 kW
17- 636076-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Trane | WSC120 | 110.2 | MBH | 4100 | CFM | 3.3 | COP(47) |  |  | 2 | HP | Electric | [5 empty] | Yes | 27 kW
17- 636076-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Trane | 4WCY5024A1000A | 22.4 | MBH | 710 | CFM | 8.3 | HSPF |  |  | 0.5 | HP | Electric | [5 empty] | Yes | 7.5 kW
17- 636076-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Trane | WSC072 | 71.5 | MBH | 2625 | CFM | 3.3 | COP(47) |  |  | 1.5 | HP | Electric | [5 empty] | Yes | 18 kW
17- 636076-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | Trane | WSC090 | 86.1 | MBH | 3150 | CFM | 3.3 | COP(47) |  |  | 2 | HP | Electric | [5 empty] | Yes | 18 kW
17- 637259-1 | Other | CRA13-18 | Liebert | DA150DP1A | [10 empty] | Electric | Split System DX | 18000 | CFM | 30 | kW | N/A | N/A
17- 637259-1 | Other | CRA25-26 | Liebert | VS042ADA000 | [10 empty] | Electric | Split System DX | 6300 | CFM | 7.5 | HP | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-1 | Lennox | EL195UH110XE60C | 104500 | Btu/hr | 2100 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-10 | Lennox | EL195UH090XE48C | 83600 | Btu/hr | 1600 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-11 | Lennox | EL195UH070XE36B | 62700 | Btu/hr | 1175 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-2 | Lennox | EL195UH110XE60C | 104500 | Btu/hr | 1900 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-3 | Lennox | EL195UH045XE24B | 41800 | Btu/hr | 800 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-4 | Lennox | EL195UH070XE36B | 62700 | Btu/hr | 1100 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-5 | Lennox | EL195UH070XE36B | 62700 | Btu/hr | 900 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-6 | Lennox | EL195UH070XE36B | 62700 | Btu/hr | 1200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-7 | Lennox | EL195UH110XE60C | 104500 | Btu/hr | 1950 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-8 | Lennox | EL195UH110XE60C | 104500 | Btu/hr | 2200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 642436-1 | Gas-fired indoor air handling unit | F-9 | Lennox | EL195UH110XE60C | 104500 | Btu/hr | 2200 | CFM | 95 | Thermal Efficiency (%) |  |  | 0.3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 653232-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Carrier | 48HC | 115 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-12 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-13 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-14 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-15 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-16 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-17 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-18 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-19 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-20 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-20B | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-21A | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-21B | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-24A | Carrier | CARRIER 48TC-TE24 STANDARD EFFICIENCY | 260 | MBH | 8000 | CFM | 320 | Heating Input Capacity (MBH) |  |  | 3.97 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-24B | Carrier | CARRIER 48TC-TE24 STANDARD EFFICIENCY | 260 | MBH | 8000 | CFM | 320 | Heating Input Capacity (MBH) |  |  | 3.97 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-25 | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1200 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.58 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-26 | Carrier | CARRIER 48ES-A30 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.47 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-27 | Carrier | CARRIER 48ES-A30 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.47 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-28 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29A | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29B | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29C | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29D | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29E | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29F | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29G | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-29H | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-30 | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 56 | MBH | 1000 | CFM | 72 | Heating Input Capacity (MBH) |  |  | 0.46 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 1600 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 505459-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 90 | MBH | 2000 | CFM | 115 | Heating Input Capacity (MBH) |  |  | 1.37 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- A1 | Daikin | MPS025B | 324 | MBH | 9000 | CFM | 81 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- A2 | Daikin | MPSA03C | 97 | MBH | 1200 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- A3 | Daikin | MPS025B | 324 | MBH | 9000 | CFM | 81 | Thermal Efficiency (%) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- B1 | Daikin | DCG150 | 161 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- B2 | Daikin | DCG150 | 161 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- B3 | Daikin | MPSA04C | 109 | MBH | 1600 | CFM | 82 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- C1 | Daikin | DCG102 | 161.2 | MBH | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- C2 | Daikin | MPSA03C | 62.2 | MBH | 1200 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- C3 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- C4 | Daikin | MPSA04C | 62.2 | MBH | 1600 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- C5 | Daikin | DCG102 | 161.2 | MBH | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- D1 | Daikin | DCG090 | 161.2 | MBH | 2800 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- D2 | Daikin | MPSA05c | 77.7 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- D3 | Daikin | MPSA05c | 77.7 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- D4 | Daikin | MPSA05c | 77.7 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- E1 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- E2 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- E3 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- E4 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- E5 | Daikin | MPSA05C | 77.7 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- F1 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- F2 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- F3 | Daikin | DCG120 | 161.3 | MBH | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 672586-1 | Gas-fired Packaged Rooftop HVAC | RTU- F4 | Daikin | MPSA05C | 77.7 | MBH | 2000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 674429-1 | Gas-fired Packaged Rooftop HVAC | RTU‐1 | TRANE | YSC102F3 | 110.84 | MBH | 3980 | CFM | 136.84 | Heating Input Capacity (Btu/hr) |  |  | 2.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 674429-1 | Gas-fired Packaged Rooftop HVAC | RTU‐2 | TRANE | YSC102F3 | 145.96 | MBH | 3900 | CFM | 182.46 | Heating Input Capacity (Btu/hr) |  |  | 2.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 674429-1 | Gas-fired Packaged Rooftop HVAC | RTU‐3 | TRANE | YSC102F3 | 88.67 | MBH | 2600 | CFM | 109.47 | Heating Input Capacity (Btu/hr) |  |  | 2.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 674429-1 | Gas-fired Packaged Rooftop HVAC | RTU‐4 | TRANE | YSD150F3 | 109.47 | MBH | 4200 | CFM | 136.84 | Heating Input Capacity (Btu/hr) |  |  | 3.31 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 674429-1 | Gas-fired Packaged Rooftop HVAC | RTU‐5 | TRANE | YSC036G3 | 44.88 | MBH | 1400 | CFM | 57.74 | Heating Input Capacity (Btu/hr) |  |  | 1.33 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 676005-1 | Gas-fired indoor air handling unit | F-1 | Carrier | 59SP5-060-14 | 58 | MBH | 1600 | CFM | 0.97 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 676005-1 | Gas-fired indoor air handling unit | F-2 | Carrier | 59SP5-060-14 | 58 | MBH | 1600 | CFM | 0.97 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 676005-1 | Gas-fired indoor air handling unit | F-3 | Carrier | 59SP5-060-14 | 58 | MBH | 1600 | CFM | 0.97 | Thermal Efficiency (%) |  |  | 0.75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 507255-1 [Corridors] | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48HC-D08 | 184 | MBH | 1950 | CFM | 82 | AFUE |  |  | 2.5 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 507255-1 [Furnace] | Gas-fired indoor air handling unit | FURN-1 | Carrier | 59TP6A060E | 58 | MBH | 1000 | CFM | 96 | Thermal Efficiency (%) |  |  | 0.75 | Motor HP | Natural Gas | [5 empty] | N/A | N/A
16- 507255-1 [Furnace] | Gas-fired indoor air handling unit | FURN-2 | Carrier | 59TP6A080E | 78 | MBH | 1400 | CFM | 96 | Thermal Efficiency (%) |  |  | 0.75 | Motor HP | Natural Gas | [5 empty] | N/A | N/A
16- 507255-1 [Furnace] | Gas-fired indoor air handling unit | FURN-3 | Carrier | 59TP6A080E | 78 | MBH | 1200 | CFM | 96 | Thermal Efficiency (%) |  |  | 0.75 | Motor HP | Natural Gas | [5 empty] | N/A | N/A
17- 697310-1 | Variable Refrigerant Flow | OCU-1 | Mitsubishi | PURY-P168TLMU-A | 130 | MBH |  |  | 3.49 | COP(47) | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
17- 716517-1 | Ductless Heat Pump | CU-1 | Mitsubishi | PUY-A36NHA4 | 35000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 716517-1 | Ductless Heat Pump | CU-2 | Mitsubishi | PUY-A36NHA4 | 35000 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 719811-1 | Gas-fired Packaged Rooftop HVAC | RTU 1 | AAON | RN | 390 | MBH | 12000 | CFM | 487 | Heating Input Capacity (MBH) |  |  | 15 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 719811-1 | Gas-fired Packaged Rooftop HVAC | RTU 2 | AAON | RN | 285 | MBH | 4560 | CFM | 352 | Heating Input Capacity (MBH) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 719811-1 | Gas-fired Packaged Rooftop HVAC | RTU 3 | AAON | RN | 285 | MBH | 4470 | CFM | 352 | Heating Input Capacity (MBH) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 640577-1 | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWA | 55 | MBH | 1300 | CFM | 8 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
16- 640577-1 | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWA | 25 | MBH | 950 | CFM | 8 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
16- 640577-1 | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWA | 33 | MBH | 1100 | CFM | 8 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
16- 640577-1 | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWA | 55 | MBH | 1300 | CFM | 8 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
16- 640577-1 | Air Source Heat Pump AHU (split system) | HP-5 | Trane | 4TWA | 29 | MBH | 1300 | CFM | 8 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
16- 640577-1 | Air Source Heat Pump AHU (split system) | HP-6 | Trane | 4TWA | 22 | MBH | 900 | CFM | 8 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
17- 777891-1 [Common area] | Variable Refrigerant Flow | AMOU-1 | Mitsubishi | PURY-P336YSLMU-A | 240 | MBH |  |  | 3.64 | COP(47) | 26.8 | SCHE |  |  | Electric | [5 empty] | N/A | N/A
17- 777891-1 [Common area] | Variable Refrigerant Flow | AMOU-2 | Mitsubishi | PURY-P336YSLMU-A | 378 | MBH |  |  | 3.19 | COP(47) | 20.4 | SCHE |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-1.1 | LG | ARNU073BGA4 | 567 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-1.2 | LG | ARNU243TLC4 | 567 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-2.1 | LG | ARNU283BGA4 | 567 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-2.2 | LG | ARNU363BGA4 | 567 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-3.1 | LG | ARNU423BGA4 | 567 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-3.2 | LG | ARNU483BRA2 | 567 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-4.1 | LG | ARNU543BRA2 | 432 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-4.2 | LG | ARNU763B8A2 | 432 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-4.3 | LG | ARNU963B8A2 | 432 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-5.1 | LG | ARNU093BGA4 | 432 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-5.2 | LG | ARNU123BGA4 | 432 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 778018-1 | Variable Refrigerant Flow | RCU-5.3 | LG | ARNU123TLC4 | 432 | MBH |  |  | 3.5 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 792314-1 | Gas-fired Packaged Rooftop HVAC | RRU-1 | Trane | RRU120E3DUA | 326 | MBH | 3800 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 792314-1 | Gas-fired Packaged Rooftop HVAC | RRU-2 | Trane | RRU240F3DFA | 651 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 792314-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YHC092 | 160 | MBH | 3200 | CFM | 80 | Thermal Efficiency (%) |  |  | 1.42 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 792314-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YHC092 | 160 | MBH | 3300 | CFM | 80 | Thermal Efficiency (%) |  |  | 1.42 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 792314-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YHC072 | 120 | MBH | 2500 | CFM | 80 | Thermal Efficiency (%) |  |  | 1.15 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-2 | Mitsubishi | PUZ-A36NKA7 | 38 | MBH |  |  | 10.4 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-3 | Mitsubishi | MUZ-GL12NA | 11.5 | MBH |  |  | 12.5 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-4 | Mitsubishi | MUZ-GL24NA | 23 | MBH |  |  | 10 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-5 | Mitsubishi | PUZ-A42NKA7 | 48 | MBH |  |  | 9.3 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-6 | Mitsubishi | PUZ-A42NKA7 | 48 | MBH |  |  | 9.3 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-7 | Mitsubishi | PUZ-A36NKA7 | 38 | MBH |  |  | 10.4 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-8 | Mitsubishi | PUZ-A30NKA7 | 32 | MBH |  |  | 11.6 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 803573-1 [Pad] | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | York | XP180C00R2A1AAA1A1 | 162 | MBH | 6000 | CFM | 3.24 | HSPF |  |  | Unknown |  | Electric | [5 empty] | Yes | 36 kW
17- 808067-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Carrier | 50KCQA04 | 35600 | Btu/hr | 895 | CFM | 8.1 | HSPF |  |  | 0.5 | HP | Electric | [5 empty] | Yes | 7.9 kW
17- 808067-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Carrier | 50TCQD08 | 86000 | Btu/hr | 3210 | CFM | 3.4 | COP(47) |  |  | 2 | HP | Electric | [5 empty] | Yes | 24 kW
17- 808067-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Carrier | 50KCQA05 | 45500 | Btu/hr | 1590 | CFM | 8 | HSPF |  |  | 1 | HP | Electric | [5 empty] | Yes | 15.8 kW
17- 808067-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Carrier | 50TCQA07 | 66000 | Btu/hr | 1940 | CFM | 3.5 | COP(47) |  |  | 2 | HP | Electric | [5 empty] | Yes | 15.8 kW
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-1 | Daikin | RPS045D | 812.5 | MBH | 15650 | CFM | Unknown |  |  |  | 30 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-10 | Daikin | RPS045D | 500 | MBH | 11200 | CFM | Unknown |  |  |  | 30 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-11 | Daikin | DPS016A | 240 | MBH | 4100 | CFM | Unknown |  |  |  | 11.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-13 | Daikin | MPS030F | 300 | MBH | 8100 | CFM | Unknown |  |  |  | 17 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-14 | Daikin | MPS040F | 800 | MBH | 8750 | CFM | Unknown |  |  |  | 10.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-15 | Daikin | DPS016A | 240 | MBH | 3630 | CFM | Unknown |  |  |  | 11.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-16 | Daikin | RPS071D | 1250 | MBH | 17960 | CFM | Unknown |  |  |  | 35 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-2 | Daikin | DPS016A | 240 | MBH | 4800 | CFM | Unknown |  |  |  | 9 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-3 | Daikin | DPS020A | 480 | MBH | 6565 | CFM | Unknown |  |  |  | 14 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-4 | Daikin | RPS063D | 812.5 | MBH | 14300 | CFM | Unknown |  |  |  | 20 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-5 | Daikin | RPS051D | 625 | MBH | 9949 | CFM | Unknown |  |  |  | 35 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-6 | Daikin | RPS045D | 400 | MBH | 9023 | CFM | Unknown |  |  |  | 27.5 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-7 | Daikin | RPS071D | 987.5 | MBH | 19218 | CFM | Unknown |  |  |  | 55 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-8 | Daikin | RPS110D | 987.5 | MBH | 25537 | CFM | Unknown |  |  |  | 75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 735523-1 [Classrooms, commons, misc.] | Gas-fired Packaged Rooftop HVAC | RTU-9 | Daikin | RPS051D | 625 | MBH | 16600 | CFM | Unknown |  |  |  | 40 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-1A | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-1B | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-1C | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-1D | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-1E | Daikin | REYQ216TTJU | 161 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-2A | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-2B | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-2C | Daikin | REYQ120TTJU | 85 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-2D | Daikin | REYQ96TTJU | 79.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 813087-1 | Variable Refrigerant Flow | HRU-2E | Daikin | REYQ192TTJU | 152.6 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 815466-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Lennox | LGH092H4MM3Y | 130320 | Btu/hr | 3250 | CFM | 72 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
17- 815466-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Lennox | LGH300H4MH3Y | 347520 | Btu/hr | 10500 | CFM | 72 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
17- 821806-1 | Gas-fired Packaged Rooftop HVAC | FUR-1 | Carrier | 59MN5A060V17-14 | 60 | MBH | 1335 | CFM | 95 | AFUE |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 821806-1 | Gas-fired Packaged Rooftop HVAC | FUR-2 | Carrier | 59MN5A060V17-20 | 80 | MBH | 1945 | CFM | 95 | AFUE |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 830379-1 | Gas-fired indoor air handling unit | F-1 | Unknown | Unknown | 42 | MBH | Unknown |  | 95 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
17- 830379-1 | Gas-fired Packaged Rooftop HVAC | RT-1 | Unknown | Unknown | 52 | MBH | Unknown |  | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
17- 830379-1 | Gas-fired Packaged Rooftop HVAC | RT-2 | Unknown | Unknown | 86 | MBH | Unknown |  | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
17- 830379-1 | Gas-fired Packaged Rooftop HVAC | RT-3 | Unknown | Unknown | 52 | MBH | Unknown |  | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
17- 832860-1 [Living area] | Variable Refrigerant Flow | VRF System A | Daikin | RQEYQ168PCTJ-HR | 166 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
17- 855496-1 [Living] | Gas-fired Packaged Rooftop HVAC | RTU-1 | AAON | RN011 | 233 | MBH | 4000 | CFM | 292 | Heating Input Capacity (Btu/hr) |  |  | 2.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 855496-1 [Living] | Gas-fired Packaged Rooftop HVAC | RTU-2 | AAON | RQ002 | 48 | MBH | 800 | CFM | 60 | Heating Input Capacity (Btu/hr) |  |  | 0.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 856087-1 | Variable Refrigerant Flow | HP-1 | Mitsubishi | PUHY-P96TLMU-A | 81 | MBH | 370 | CFM | 4.27 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
17- 866279-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YSC06CE4-e | 98 | MBH | 2000 | CFM | 80 | AFUE |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 866279-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YSC036CE4-e | 48 | MBH | 1220 | CFM | 80 | AFUE |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 866279-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YSC036CE4-e | 48 | MBH | 1220 | CFM | 80 | AFUE |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 686039-1 | Gas-fired Packaged Rooftop HVAC | South-2 | Lennox | ZGA120S4BS1Y | 130000 | Btu/hr |  |  | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
18- 542998-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | AAON | RN-009-2-0-E60E-569 | 230000 | Btu/hr |  |  | 3.3 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 560625-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48LC-14 | 178 | MBH | 5000 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.76 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 560625-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48LC-12 | 146 | MBH | 4250 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.86 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 571936-1 | Air Source Heat Pump AHU (split system) | CU-1 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 9 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 4 kW
18- 571936-1 | Air Source Heat Pump AHU (split system) | CU-2 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 9 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 4 kW
18- 571936-1 | Air Source Heat Pump AHU (split system) | CU-3 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 9 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 4 kW
18- 571936-1 | Air Source Heat Pump AHU (split system) | CU-4 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 9 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 4 kW
18- 576787-1 | Ductless Heat Pump | CU-1 | Mitsubishi | PUMY-P36NKMU1 | 42 | MBH |  |  | 10.5 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 576787-1 | Ductless Heat Pump | CU-2 | Mitsubishi | PUMY-P60NKMU1 | 66 | MBH |  |  | 10.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 576787-1 | Ductless Heat Pump | CU-3 | Mitsubishi | PUMY-P60NKMU1 | 66 | MBH |  |  | 10.7 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 585712-1 | Variable Refrigerant Flow | HP-1 | LG | ARWB336DAS4 | 387300 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 585712-1 | Variable Refrigerant Flow | HP-2 | LG | ARWB192DAS4 | 186500 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 585712-1 | Variable Refrigerant Flow | HP-3 | LG | ARWB288DAS4 | 292900 | Btu/hr |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 612115-1 | Air Source Heat Pump AHU (split system) | HP-1 | Daikin | DZ | 18000 | Btu/hr | 600 | CFM | 3.8 | COP(47) |  |  |  |  | Electric | [5 empty] | Yes | 5 kW
18- 612115-1 | Air Source Heat Pump AHU (split system) | HP-2 | Daikin | DZ | 23200 | Btu/hr | 840 | CFM | 3.8 | COP(47) |  |  |  |  | Electric | [5 empty] | Yes | 7.5 kW
18- 612115-1 | Air Source Heat Pump AHU (split system) | HP-3 | Daikin | DZ | 60000 | Btu/hr | 1800 | CFM | 3.8 | COP(47) |  |  |  |  | Electric | [5 empty] | Yes | 17 kW
18- 612115-1 | Air Source Heat Pump AHU (split system) | HP-4 | Daikin | DZ | 36000 | Btu/hr | 262 | CFM | 3.9 | COP(47) |  |  |  |  | Electric | [5 empty] | Yes | 15 kW
18- 625157-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YSC09H3RMA | 122 | MBH | 3000 | CFM | Unknown |  |  |  | 0.67 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 641081-1 | Zonal Electric | CD2-ADH-BR1 | Warren Technology | CBK-SLIP-IN | 20 | kW |  |  | N/A | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 641081-1 | Zonal Electric | CD2-EDH-AR1 | Warren Technology | CBK-SLIP-IN | 20 | kW |  |  | N/A | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 641081-1 | Zonal Electric | CD2-EDH-AR2 | Warren Technology | CBK-SLIP-IN | 20 | kW |  |  | N/A | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 641081-1 | Zonal Electric | CD2-EDH-BR2 | Warren Technology | CBK-SLIP-IN | 20 | kW |  |  | N/A | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 641081-1 | Zonal Electric | CD2-EDH-BR3 | Warren Technology | CBK-SLIP-IN | 20 | kW |  |  | N/A | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R11 | LG | Arum | 72 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R12 | LG | Arum | 68 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R21 | LG | Arum | 162 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R22 | LG | Arum | 66 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R31 | LG | Arum | 58 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R32 | LG | Arum | 22 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R41 | LG | Arum | 58 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R42 | LG | Arum | 22 | MBH |  |  | 4.28 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R51 | LG | Arum | 62 | MBH |  |  | 4.01 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R52 | LG | Arum | 44 | MBH |  |  | 4.01 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R61 | LG | Arum | 60 | MBH |  |  | 4.01 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R62 | LG | Arum | 84 | MBH |  |  | 4.01 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R63 | LG | Arun | 2 | MBH |  |  | 4.01 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 650512-1 | Variable Refrigerant Flow | OU-R64 | LG | Arun | 0 | MBH |  |  | 3.92 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 596289-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Lennox | LGH156H4M | 288000 | Btu/hr | 5100 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596289-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Lennox | LGH156H4M | 288000 | Btu/hr | 5100 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596289-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Lennox | LGH156H4M | 288000 | Btu/hr | 5100 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596289-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Lennox | LGH156H4M | 288000 | Btu/hr | 5100 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596289-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Lennox | LGH092H4M | 192000 | Btu/hr | 3200 | CFM | 80 | Thermal Efficiency (%) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-1-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-1-2 | Mitsubishi | PURY-216YLMU-A | 230000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-2-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-2-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-3-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-3-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-4-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-4-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-5-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-5-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-6-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-6-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-7-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-7-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-8-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-8-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-9-1 | Mitsubishi | PURY-336YLMU-A | 378000 | Btu/hr |  |  | 3.23 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 704117-1 | Variable Refrigerant Flow | HP-9-2 | Mitsubishi | PURY-168YLMU-A | 188000 | Btu/hr |  |  | 3.49 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [AHU] | Other | RTU-1 | Daikin | RPS045D | [10 empty] | Electric | Electric Heat w/ Dx AHU | 124 | MBH | 27.5 | HP | N/A | N/A
18- 718226-1 [AHU] | Other | RTU-2 | Daikin | RPS045D | [10 empty] | Electric | Electric Heat w/ Dx AHU | 125 | MBH | 27.5 | HP | N/A | N/A
18- 718226-1 [AHU] | Other | RTU-3 | Daikin | RPS035D | [10 empty] | Electric | Electric Heat w/ Dx AHU | 63 | MBH | 30 | HP | N/A | N/A
18- 718226-1 [AHU] | Other | RTU-4 | Daikin | RPS021D | [10 empty] | Electric | Electric Heat w/ Dx AHU | 63 | MBH | 20 | HP | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-1 | Mitsubishi | PUZ-A36 | 37 | MBH |  |  | 9.3 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-2 | Mitsubishi | PUZ-A30 | 32 | MBH |  |  | 8.9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-3 | Mitsubishi | PUZ-A24 | 26 | MBH |  |  | 10.8 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-4 | Mitsubishi | PUZ-A42 | 45 | MBH |  |  | 9.3 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-5 | Mitsubishi | PUZ-A30 | 32 | MBH |  |  | 8.9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-6 | Mitsubishi | PUZ-A36 | 37 | MBH |  |  | 9.3 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718226-1 [DHP] | Ductless Heat Pump | CU-7 | Mitsubishi | PUZ-A30 | 32 | MBH |  |  | 8.9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-1 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 2.93 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-2 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 2.93 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-3 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 2.99 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-4 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 2.99 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-5 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 2.99 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-6 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 2.99 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-7 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 2.93 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-8 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 2.93 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 718902-1 | Air Source Heat Pump AHU (split system) | HP-9 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 2.93 | COP(47) |  |  |  |  | Electric | [5 empty] | Unknown | Unknown
18- 723839-1 | Variable Refrigerant Flow | HP-1 | LG | ARUM168BTE5 | 189000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 723839-1 | Variable Refrigerant Flow | HP-2 | LG | ARUM241BTE5 | 222000 | Btu/hr |  |  | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-1 | York | THE418B31S | 31.6 | MBH | 1500 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 10.8 kW
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-2 | York | YHE24B21S | 15.1 | MBH | 750 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 5.8 kW
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-3 | York | THE60B31S | 40.3 | MBH | 1900 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 13.2 kW
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-4 | York | THE60B31S | 40.3 | MBH | 1900 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 13.2 kW
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-5 | York | THE30B31S | 19.6 | MBH | 900 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 7.2 kW
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-6 | York | THE36B31S | 19.9 | MBH | 1100 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 7.2 kW
18- 737861-1 | Air Source Heat Pump AHU (split system) | HP-7 | York | THE48B31S | 29.5 | MBH | 1550 | CFM | 8.2 | HSPF | N/A |  |  |  | Electric | [5 empty] | Yes | 10.8 kW
18- 785631-1 | Gas-fired Packaged Rooftop HVAC | 36-RTU-01 | Carrier | 48LCE20 | 220.9 | MBH | 7000 | CFM | 81 | Thermal Efficiency (%) |  |  | 13.93 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 785631-1 | Gas-fired Packaged Rooftop HVAC | 36-RTU-02 | Carrier | 48LCE20 | 220.9 | MBH | 7000 | CFM | 81 | Thermal Efficiency (%) |  |  | 13.93 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 785631-1 | Gas-fired Packaged Rooftop HVAC | 36-RTU-03 | Carrier | 48LCE20 | 220.9 | MBH | 7000 | CFM | 81 | Thermal Efficiency (%) |  |  | 13.93 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 811956-1 | Air Source Heat Pump AHU (split system) | HP-1 | Lennox | 14HPX-024-230 | 21800 | Btu/hr | 900 | CFM | 9 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 11.3 kW
18- 863748-1 | Variable Refrigerant Flow | VRF-01 | Mitsubishi | Unknown | 20 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-02 | Mitsubishi | Unknown | 17 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-03 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-04 | Mitsubishi | Unknown | 13.5 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-05 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-06 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-07 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-08 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-09 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-10 | Mitsubishi | Unknown | 7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-11 | Mitsubishi | Unknown | 9 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-12 | Mitsubishi | Unknown | 9 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 863748-1 | Variable Refrigerant Flow | VRF-13 | Mitsubishi | Unknown | 9 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-0.1 | Carrier | 48HC-017 | 584 | MBH | 6000 | CFM | 81 | Thermal Efficiency (%) |  |  | 4.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-0.2 | Carrier | 48HC-009 | 331 | MBH | 3400 | CFM | 82 | Thermal Efficiency (%) |  |  | 3.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-1.1 | Carrier | 48HC-009 | 331 | MBH | 3400 | CFM | 82 | Thermal Efficiency (%) |  |  | 2.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-1.2 | Carrier | 48HC-005 | 159 | MBH | 1600 | CFM | 81 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-2.1 | Carrier | 48HC-004 | 159 | MBH | 1200 | CFM | 81 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-2.2 | Carrier | 48HC-008 | 331 | MBH | 3000 | CFM | 82 | Thermal Efficiency (%) |  |  | 2.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-3.1 | Carrier | 48HC-008 | 331 | MBH | 3000 | CFM | 82 | Thermal Efficiency (%) |  |  | 2.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-3.2 | Carrier | 48HC-017 | 584 | MBH | 6000 | CFM | 81 | Thermal Efficiency (%) |  |  | 2.9 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-3.3 | Carrier | 48HC-006 | 159 | MBH | 2000 | CFM | 81 | Thermal Efficiency (%) |  |  | 2.4 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-3.4 | Carrier | 48HC-008 | 331 | MBH | 3000 | CFM | 82 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 899620-1 | Gas-fired Packaged Rooftop HVAC | RTU-3.5 | Carrier | 48HC-007 | 204 | MBH | 2400 | CFM | 80 | Thermal Efficiency (%) |  |  | 1.7 | BHP | Natural Gas | [5 empty] | N/A | N/A
19- 672421-1 | Ductless Heat Pump | HP-1B | Mitsubishi | PUZ-A18NKA7 | 23 | MBH |  |  | 3.78 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YSC072 | 57.33 | MBH | 2250 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Trane | YSD150 | 107.5 | MBH | 4500 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Trane | YSD210 | 179.16 | MBH | 7875 | CFM | 80 | Thermal Efficiency (%) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-12 | Trane | YSH180 | 179.16 | MBH | 6750 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-13 | Trane | YSD150 | 112.5 | MBH | 4500 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-14 | Trane | YSC036 | 44.07 | MBH | 1350 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-15 | Trane | YSC036 | 44.07 | MBH | 1350 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-16 | Trane | YSC036 | 44.07 | MBH | 1350 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YSC072 | 57.33 | MBH | 2250 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YSC072 | 57.33 | MBH | 2250 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | YSC048 | 44.07 | MBH | 1800 | CFM | 81 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Trane | YSD150 | 107.5 | MBH | 4500 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Trane | YSD150 | 107.5 | MBH | 4500 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Trane | YSD150 | 107.5 | MBH | 4500 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Trane | YSD150 | 107.5 | MBH | 4500 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 700419-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Trane | YSC072 | 58.05 | MBH | 2250 | CFM | 81 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-1 | LG | ARUM241DTE5 | 243 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-1.1 | LG | ARUM384DTE5 | 432 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-1.2 | LG | ARUM384DTE5 | 432 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-2.1 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-2.2 | LG | ARUM336DTE5 | 378 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-2.3 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-3 | LG | ARUM241DTE5 | 243 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-3.1 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-3.2 | LG | ARUM336DTE5 | 378 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-3.3 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-4.1 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-4.2 | LG | ARUM336DTE5 | 378 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 730078-1 | Variable Refrigerant Flow | RCU-4.3 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
19- 731945-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Carrier | 50KCQA06 | 20.7 | MBH | 2000 | CFM | 8.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
19- 731945-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Carrier | 50HCQD07 | 23.2 | MBH | 2000 | CFM | 8.2 | HSPF | 3.5 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
19- 731945-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Carrier | 50TCQD12 | 48 | MBH | 4000 | CFM | 7.7 | HSPF | 3.4 | COP(47) |  |  | Electric | [5 empty] | N/A | N/A
19- 731945-1 | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Carrier | 50KCQA06 | 23.7 | MBH | 2000 | CFM | 8.2 | HSPF |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#1 | Lennox | KGA120H4BM-G | 144000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#10 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#11 | Lennox | KGB048S4DM-G | 86000 | Btu/hr | 1600 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#12 | Lennox | KGB048S4DM-G | 86000 | Btu/hr | 1600 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#2 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#3 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#4 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#5 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#6 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#7 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#8 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 596300-1 | Gas-fired Packaged Rooftop HVAC | HL#9 | Lennox | KGA120H4BS-G | 104000 | Btu/hr | 4000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 765123-1 | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWV8036A | 36900 | Btu/hr | 1400 | CFM | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
19- 765123-1 | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWR4030G | 36900 | Btu/hr | 1200 | CFM | 2.7 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
19- 765123-1 | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWV8036A | 36900 | Btu/hr | 1400 | CFM | 3.2 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
19- 937126-1 | Gas-fired Packaged Rooftop HVAC | AC#1 | Lennox | LGH300H4M | 288 | MBH | 10000 | CFM | 360 | Heating Input Capacity (Btu/hr) |  |  | 10 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 937126-1 | Gas-fired Packaged Rooftop HVAC | AC#2 | Lennox | LGH094U4M | 192 | MBH | 3000 | CFM | 240 | Heating Input Capacity (Btu/hr) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
19- 937126-1 | Gas-fired Packaged Rooftop HVAC | AC#3 | Lennox | LGH300H4M | 288 | MBH | 8000 | CFM | 360 | Heating Input Capacity (Btu/hr) |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-1N | Mitsubishi | PURY-P288YSKMU-A | 24 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-1S | Mitsubishi | PURY-P288YSKMU-A | 24 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-2/3N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-2/3SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-2/3W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-2N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-2SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-2W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-3/4N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-3/4SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-3/4W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-3N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-3SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-3W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-4N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-4SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-4W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-5/6N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-5/6SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-5/6W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-5N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-5SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-5W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-6N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-6SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
98- 927699-1 | Variable Refrigerant Flow | HP-6W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown | [5 empty] | Electric | 0 |  |  |  |  | N/A | N/A
18- 908206-1 | Air Source Heat Pump (Packaged Rooftop) | HP-1 | Carrier | 50HCQD08 | 62 | MBH | 3000 | CFM | Unknown |  |  |  | 1.03 | BHP | Electric | [5 empty] | Yes | 24 kW
15- 689971-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YSC | 61 | MBH | 1990 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
15- 689971-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YSC | 27 | MBH | 1400 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
15- 689971-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YSC | 37 | MBH | 1600 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
15- 689971-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | YSC | 52 | MBH | 1990 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
15- 689971-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Trane | YSC | 59 | MBH | 2800 | CFM | 80 | Thermal Efficiency (%) |  |  |  |  | Natural Gas | [5 empty] | N/A | N/A
19- 506267-1 | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWA4036A3 | 3 | Tons | 1190 | CFM | 8.2 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 7.2 kW
19- 506267-1 | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWA4060A3 | 5 | Tons | 1840 | CFM | 8.5 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 7.2 kW
19- 506267-1 | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWA4060A3 | 5 | Tons | 1840 | CFM | 8.5 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 7.2 kW
19- 506267-1 | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWA4060A3 | 5 | Tons | 1840 | CFM | 8.5 | HSPF |  |  |  |  | Electric | [5 empty] | Yes | 7.2 kW
14- 579875-1 | Ductless Heat Pump | CU-1 | Carrier | 25HCE448A003 | 49.3 | MBH |  |  | 8.2 | HSPF | Unknown |  |  |  | Electric | [5 empty] | N/A | N/A
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-1 | Trane | 4TTR6024 | 2 | Tons | 850 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 4.8 kW
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-2 | Trane | 4TTR6018 | 1.5 | Tons | 615 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 7.68 kW
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-3 | Trane | 4TTR6024 | 1.5 | Tons | 840 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 4.8 kW
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-4 | Trane | 4TTR6048 | 4 | Tons | 1660 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 4.8 kW
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-5 | Trane | 4TTR6048 | 4 | Tons | 1720 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 4.8 kW
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-6 | Trane | 4TTR6030 | 2.5 | Tons | 1150 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 4.8 kW
18- 625974-1 | Air Source Heat Pump AHU (split system) | CU-7 | Trane | 4TTR6042 | 3.5 | Tons | 1450 | CFM | Unknown | [5 empty] | Electric | [5 empty] | Yes | 4.8 kW
19- 912980-1 | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWR6036 | 33.2 | MBH | 1200 | CFM | 9.6 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
19- 912980-1 | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWR6036 | 33.2 | MBH | 1200 | CFM | 9.6 | HSPF |  |  |  |  | Electric | [5 empty] | No | N/A
16- 709134-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | SF-090 | 680 | MBH | 40000 | CFM | 80 | Thermal Efficiency (%) |  |  | 75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 709134-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | SF-090 | 680 | MBH | 40000 | CFM | 80 | Thermal Efficiency (%) |  |  | 75 | HP | Natural Gas | [5 empty] | N/A | N/A
16- 709134-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YHD300 | 200 | MBH | 10000 | CFM | 90 | Thermal Efficiency (%) |  |  | 10.5 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 554364-1 [Administrative] | Variable Refrigerant Flow | HP-1 | Mitsubishi | PURY-P336YSLMU-A | 245.7 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 554364-1 [Administrative] | Variable Refrigerant Flow | HP-2 | Mitsubishi | PURY-P336YSLMU-A | 253.8 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
18- 554364-1 [Kitchen & Whitebox] | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48A2-027 High Efficiency | 374 | MBH | 10000 | CFM | 525 | Heating Input Capacity (Btu/hr) |  |  | 4.82 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 554364-1 [Kitchen & Whitebox] | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48HC-D08 High Efficiency | 331 | MBH | 3000 | CFM | 404 | Heating Input Capacity (Btu/hr) |  |  | 2.39 | BHP | Natural Gas | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-1-1 | LG | ARUN060GSS4 | 64 | MBH |  |  | 10 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-1-2 | LG | LSN360HV | 38.9 | MBH |  |  | 9.9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-7-2 | LG | ARUN024GSS4 | 27.3 | MBH |  |  | 8.6 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-7-3 | LG | ARUN048GSS4 | 53.9 | MBH |  |  | 9.5 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-R-1 | LG | LSU360HV | 38.9 | MBH |  |  | 9.9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-R-2 | LG | ARUN038GSS4 | 38.6 | MBH |  |  | 9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 442030-1 | Ductless Heat Pump | CU-R-3 | LG | ARUN038GSS4 | 28 | MBH |  |  | 9 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
16- 615127-1 | Variable Refrigerant Flow | CU-1 | LG | ARUB384DTE4 | 442.5 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
16- 615127-1 | Variable Refrigerant Flow | CU-2 | LG | ARUB337DTE4 | 387.5 | MBH |  |  | Unknown | [5 empty] | Electric | [5 empty] | N/A | N/A
08- 723130-1 | Variable Refrigerant Flow | CU-1 | LG | ARUB144BTE4 | 144 | MBH |  |  | 3.8 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
12- 456419-1 | Other | FC-1 | Bryant | FX4C-042 | [10 empty] | Electric | Electric Forced Air Furnace | 10 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-10 | Bryant | FF1E024-05 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-11 | Bryant | FF1E036-05 | [10 empty] | Electric | Electric Forced Air Furnace | 7.5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-12 | Bryant | FF1E030-05 | [10 empty] | Electric | Electric Forced Air Furnace | 7.5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-13 | Bryant | FF1E030-05 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-14 | Bryant | FF1E030-05 | [10 empty] | Electric | Electric Forced Air Furnace | 7.5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-15 | Bryant | FX4C-024 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-2 | Bryant | FX4C-036 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-3 | Bryant | FX4C-042 | [10 empty] | Electric | Electric Forced Air Furnace | 15 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-4 | Bryant | FX4C-042 | [10 empty] | Electric | Electric Forced Air Furnace | 15 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-5 | Bryant | FX4C-060 | [10 empty] | Electric | Electric Forced Air Furnace | 10 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-6 | Bryant | FX4C-060 | [10 empty] | Electric | Electric Forced Air Furnace | 10 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-7 | Bryant | FF1E036-05 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-8 | Bryant | FF1E024-05 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
12- 456419-1 | Other | FC-9 | Bryant | FF1E024-05 | [10 empty] | Electric | Electric Forced Air Furnace | 5 | kW | N/A | N/A | N/A | N/A
18- 614250-1 | Variable Refrigerant Flow | VRF-HP-1 | LG | ARUM 264DTE5 | 282 | MBH |  |  | 3.6 | COP(47) | 2.5 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
18- 614250-1 | Variable Refrigerant Flow | VRF-HP-2 | LG | ARUM 216DTE5 | 230 | MBH |  |  | 3.5 | COP(47) | 2.7 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
18- 614250-1 | Variable Refrigerant Flow | VRF-HP-3 | LG | ARUM 121DTE5 | 129 | MBH |  |  | 4 | COP(47) | 2.7 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
18- 535655-1 | Gas-fired Packaged Rooftop HVAC | AC#1 | Lennox | LGH240H4B | 384 | MBH | 8000 | CFM | 80 | AFUE |  |  | 7.5 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 535655-1 | Gas-fired Packaged Rooftop HVAC | AC#2 | Lennox | LGH152U4E | 192 | MBH | 5000 | CFM | 80 | AFUE |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 535655-1 | Gas-fired Packaged Rooftop HVAC | AC#3 | Lennox | LGH152U4E | 192 | MBH | 5000 | CFM | 80 | AFUE |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Natatorium] | Gas-fired Packaged Rooftop HVAC | AHU-1 | INNOVENT | NDHU | 437 | MBH | 23150 | CFM | 96.2 | AFUE |  |  | 21.6 | BHP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Other] | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YZC090 | 162 | MBH | 3000 | CFM | 80 | AFUE |  |  | 2.75 | BHP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Other] | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YZC072 | 97.2 | MBH | 2500 | CFM | 80 | AFUE |  |  | 1.08 | BHP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Other] | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | RF050434 | 769 | MBH | 21050 | CFM | 81 | AFUE |  |  | 28.14 | BHP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Other] | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | YZC048 | 64 | MBH | 1780 | CFM | 80 | AFUE |  |  | 0.92 | BHP | Natural Gas | [5 empty] | N/A | N/A
19- 820425-1 | Variable Refrigerant Flow | CU-1 | LG | ARUN121BTE5 | 135000 | Btu/hr |  |  | Unknown |  | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
18- 577317-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | York | ZJ102 | 144 | MBH | 2975 | CFM | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
18- 577317-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | York | ZJ102 | 144 | MBH | 2975 | CFM | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
18- 577317-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | York | ZJ102 | 144 | MBH | 3400 | CFM | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
18- 577317-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | York | ZJ078 | 96 | MBH | 2600 | CFM | 80 | Thermal Efficiency (%) |  |  | Unknown |  | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Trane | YSD150 | 192 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-10 | Trane | YSD036 | 104 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-11 | Trane | YSD036 | 104 | MBH | 1200 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Trane | YSD150 | 192 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Trane | YSD150 | 192 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Trane | YSD150 | 192 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-5 | Trane | YSD150 | 192 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-6 | Trane | YSD150 | 192 | MBH | 5000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-7 | Trane | YSD090 | 104 | MBH | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-8 | Trane | YSD090 | 104 | MBH | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 3 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 799406-1 | Gas-fired Packaged Rooftop HVAC | RTU-9 | Trane | YSD072 | 104 | MBH | 2400 | CFM | 80 | Thermal Efficiency (%) |  |  | 1.5 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-1 | York | ZYG05E2B1AA2B111A2 | 90 | MBH | 1400 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.74 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-2 | York | ZYG08E2B3AA2B111A2 | 144 | MBH | 2700 | CFM | 80 | Thermal Efficiency (%) |  |  | 1.25 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-3 | York | ZYG08E2B3AA2B111A2 | 144 | MBH | 2250 | CFM | 80 | Thermal Efficiency (%) |  |  | 0.94 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-6 | York | ZF180N30R2D1EAA1A1 | 240 | MBH | 7000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-7 | York | ZF180N30R2D1EAA1A1 | 240 | MBH | 7000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-8 | York | ZF180N30R2D1EAA1A1 | 240 | MBH | 7000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 563561-1 | Gas-fired Packaged Rooftop HVAC | G-RTU-9 | York | ZF180N30R2D1EAA1A1 | 240 | MBH | 7000 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | BHP | Natural Gas | [5 empty] | N/A | N/A
17- 551538-3 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Lennox | LGH180H4M | 480 | MBH | 6000 | CFM | 480 | Heating Input Capacity (MBH) |  |  | 5 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 551538-3 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Lennox | LGH092H4M | 240 | MBH | 3000 | CFM | 240 | Heating Input Capacity (MBH) |  |  | 2 | HP | Natural Gas | [5 empty] | N/A | N/A
17- 701880-1 | Variable Refrigerant Flow | CU-01 | Daikin | RELQ192TATJU | 136.7 | MBH |  |  | 3.85 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
18- 863366-1 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48HCF09A | 161.9 | MBH | 3400 | CFM | 197.1 | Heating Input Capacity (MBH) |  |  | 1.58 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 863366-1 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48HCF09A | 161.9 | MBH | 3400 | CFM | 197.1 | Heating Input Capacity (MBH) |  |  | 1.58 | BHP | Natural Gas | [5 empty] | N/A | N/A
18- 863366-1 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48FCF06A | 105 | MBH | 2000 | CFM | 132 | Heating Input Capacity (MBH) |  |  | 0.95 | BHP | Natural Gas | [5 empty] | N/A | N/A
14- 689118-1 | Variable Refrigerant Flow | CU-1 | Daikin | REYQ336TTJU | 378 | MBH |  |  | 3.5 | COP(47) | 2.2 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
14- 689118-1 | Variable Refrigerant Flow | CU-2 | Daikin | REYQ288TTJU | 324 | MBH |  |  | 3.5 | COP(47) | 2.4 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
14- 689118-1 | Variable Refrigerant Flow | CU-3 | Daikin | REYQ144TTJU | 162 | MBH |  |  | 3.8 | COP(47) | 24.2 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
14- 689118-1 | Variable Refrigerant Flow | CU-4 | Daikin | REYQ144TTJU | 162 | MBH |  |  | 3.8 | COP(47) | 24.2 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 550764-1 | Ductless Heat Pump | ACCU-401 | Mitsubishi | PEAD/PUZ | 38 | MBH |  |  | 4.62 | COP(47) | 2.6 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 550764-1 | Ductless Heat Pump | ACCU-402 | Mitsubishi | PEAD/PUZ | 28 | MBH |  |  | 4.35 | COP(47) | 2.66 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 550764-1 | Ductless Heat Pump | ACCU-403 | Mitsubishi | PEAD/PUZ | 48 | MBH |  |  | 4.62 | COP(47) | 2.6 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
17- 550764-1 | Ductless Heat Pump | ACCU-407 | Mitsubishi | PEAD/PUZ | 19 | MBH |  |  | 3.97 | COP(47) | 2.38 | COP(17) |  |  | Electric | [5 empty] | N/A | N/A
15- 568036-2 | Gas-fired Packaged Rooftop HVAC | RTU-1 | Carrier | 48TCTA07 | 120 | MBH | 2220 | CFM | 80 | AFUE |  |  | 1.03 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 568036-2 | Gas-fired Packaged Rooftop HVAC | RTU-2 | Carrier | 48TCTA07 | 120 | MBH | 2220 | CFM | 80 | AFUE |  |  | 1.03 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 568036-2 | Gas-fired Packaged Rooftop HVAC | RTU-3 | Carrier | 48TCTA07 | 120 | MBH | 2220 | CFM | 80 | AFUE |  |  | 1.03 | BHP | Natural Gas | [5 empty] | N/A | N/A
15- 568036-2 | Gas-fired Packaged Rooftop HVAC | RTU-4 | Carrier | 48TCTA07 | 120 | MBH | 2220 | CFM | 80 | AFUE |  |  | 1.03 | BHP | Natural Gas | [5 empty] | N/A | N/A
19- 550436-1 | Variable Refrigerant Flow | CU-1 | Mitsubishi | PURY-HP192TSKMU-A-H | 15.3 | Tons |  |  | 3.31 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
19- 550436-1 | Variable Refrigerant Flow | CU-2 | Mitsubishi | PURY-HP192TSKMU-A-H | 15.7 | Tons |  |  | 3.31 | COP(47) |  |  |  |  | Electric | [5 empty] | N/A | N/A
13- 658146-1 [Natatorium] | Gas-fired Packaged Rooftop HVAC | RTU R.1 | Trane | YZC090 | 162 | MBH | 3000 | CFM | 80 | Thermal Efficiency (%) |  |  | 2.75 | HP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Natatorium] | Gas-fired Packaged Rooftop HVAC | RTU R.2 | Trane | YZC072 | 97.2 | MBH | 2500 | CFM | 80 | Thermal Efficiency (%) |  |  | 2.75 | HP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Natatorium] | Gas-fired Packaged Rooftop HVAC | RTU R.3 | Trane | RF050434 | 768 | MBH | 21050 | CFM | 80 | Thermal Efficiency (%) |  |  | 30 | HP | Natural Gas | [5 empty] | N/A | N/A
13- 658146-1 [Natatorium] | Gas-fired Packaged Rooftop HVAC | RTU R.4 | Trane | YZC048 | 64 | MBH | 1780 | CFM | 80 | Thermal Efficiency (%) |  |  | 1 | HP | Natural Gas | [5 empty] | N/A | N/A
18- 559771-1 | Ductless Heat Pump | DSS-1 | Mitsubishi | SUZ-KA15NA | 18000 | Btu/hr |  |  | 9.6 | HSPF | N/A |  |  |  | Electric | [5 empty] | N/A | N/A
11- 556107-1 | Gas-fired indoor air handling unit | AHU-1 | AAON | RN-060-3-0-EA09-3D9 | 648 | MBH | 22000 | CFM |  | 80 | AFUE |  | 12.39 | BHP | Natural Gas | [5 empty] | N/A | N/A
11- 556107-1 | Gas-fired indoor air handling unit | AHU-1 | AAON | RN-060-3-0-EA09-3D9 | 648 | MBH | 22000 | CFM |  | 80 | AFUE |  | 12.39 | BHP | Natural Gas | [5 empty] | N/A | N/A

## Stage2Cooling
Project_ID | Equipment_Type_short | Equipment Type | Equipment ID | Manufacturer | Model | Capacity_Metric_1 | Capacity_Metric_1_Units | Capacity_Metric_2 | Capacity_Metric_2_Units | Efficiency_Metric_1 | Efficiency_Metric_1_Units | Efficiency_Metric_2 | Efficiency_Metric_2_Units | Fuel Type | Fan Control | VRF Heat Recovery?
07- 782313-1 | VRF | Variable Refrigerant Flow | HP-CS | Mitsubishi | PURY-P96 | 96 | MBH |  |  | 15.5 | EER | 22.1 | IEER | Electric | N/A | No
07- 782313-1 | VRF | Variable Refrigerant Flow | HP-K | Mitsubishi | PURY-P168 | 168 | MBH |  |  | 15.5 | EER | 22.1 | IEER | Electric | N/A | No
07- 782313-1 | VRF | Variable Refrigerant Flow | HP-K2 | Mitsubishi | PURY-P336 | 288 | MBH |  |  | 12.7 | EER | 20.9 | IEER | Electric | N/A | No
07- 782313-1 | VRF | Variable Refrigerant Flow | HP-K3 | Mitsubishi | PURY-P336 | 288 | MBH |  |  | 12.7 | EER | 20.9 | IEER | Electric | N/A | No
07- 782313-1 | VRF | Variable Refrigerant Flow | HP-K4 | Mitsubishi | PURY-P72 | 72 | MBH |  |  | 15.5 | EER | 22.1 | IEER | Electric | N/A | No
07- 782313-1 | VRF | Variable Refrigerant Flow | HP-P | Mitsubishi | PURY-P144 | 72 | MBH |  |  | 15.5 | EER | 22.1 | IEER | Electric | N/A | No
09- 581175-1 | VRF | Variable Refrigerant Flow | ODU | Mitsubishi | PURY-P-240TSMU-A | 240 | MBH |  |  | 11.7 | EER | 18 | SEER | Electric | N/A | Yes
11- 468179-1 | DHP | Ductless Heat Pump | DHP-1 | Daikin | FTXS24LVJU | 21400 | Btu/hr |  |  | 20 | SEER | 12.5 | EER | Electric | N/A | N/A
11- 468179-1 | DHP | Ductless Heat Pump | DHP-2 | Daikin | FTXS24LVJU | 21400 | Btu/hr |  |  | 20 | SEER | 12.5 | EER | Electric | N/A | N/A
11- 468179-1 | DHP | Ductless Heat Pump | DHP-3 | Daikin | FTXS24LVJU | 21400 | Btu/hr |  |  | 20 | SEER | 12.5 | EER | Electric | N/A | N/A
11- 531122-1 | DHP | Ductless Heat Pump | HP-2 | Daikin | FXAQ | 45.6 | MBH |  |  | 18 | EER |  |  | Electric | N/A | N/A
11- 531122-1 | DHP | Ductless Heat Pump | HP-1 | Daikin | FXAQ | 45.6 | MBH |  |  | 18 | EER |  |  | Electric | N/A | N/A
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-01 | Trane | 4TVR0240B300NB | 240000 | Btu/hr |  |  | 10.6 | EER | 19.1 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-02 | Trane | 4TVR0168B400NB | 168000 | Btu/hr |  |  | 11.4 | EER | 20.8 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-03 | Trane | 4TVR0144B300NB | 144000 | Btu/hr |  |  | 10.8 | EER | 21.1 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-04 | Trane | 4TVR0120B300NB | 120000 | Btu/hr |  |  | 11.1 | EER | 21.8 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-05 | Trane | 4TVR0168B400NB | 168000 | Btu/hr |  |  | 11.4 | EER | 20.8 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-06 | Trane | 4TVR0144B300NB | 144000 | Btu/hr |  |  | 10.8 | EER | 21.1 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-07 | Trane | 4TVR0168B400NB | 168000 | Btu/hr |  |  | 11.4 | EER | 20.8 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-08 | Trane | 4TVR0144B300NB | 144000 | Btu/hr |  |  | 10.8 | EER | 21.1 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-09 | Trane | 4TVR0168B400NB | 168000 | Btu/hr |  |  | 11.4 | EER | 20.8 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-10 | Trane | 4TVR0144B300NB | 144000 | Btu/hr |  |  | 10.8 | EER | 21.1 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-11 | Trane | 4TVR0168B400NB | 168000 | Btu/hr |  |  | 11.4 | EER | 20.8 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-12 | Trane | 4TVR0144B300NB | 144000 | Btu/hr |  |  | 10.8 | EER | 21.1 | IEER | Electric | N/A | No
11- 631833-2 | VRF | Variable Refrigerant Flow | ACCU-13 | Trane | 4TVR0120B300NB | 120000 | Btu/hr |  |  | 11.1 | EER | 21.8 | IEER | Electric | N/A | No
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-1 | Guardian | THE36B31S | 3 | Tons | 1200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-2 | Guardian | THE60B31S | 5 | Tons | 1900 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-3 | Guardian | THE48B31S | 4 | Tons | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-4 | Guardian | THE48B31S | 4 | Tons | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-5 | Guardian | THE60B31S | 5 | Tons | 1900 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-6 | Guardian | THE36B31S | 3 | Tons | 1200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-7 | Guardian | THE60B31S | 5 | Tons | 1625 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-8 | Guardian | THE36B31S | 3 | Tons | 1200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-9 | Guardian | THE60B31S | 5 | Tons | 1900 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-10 | Guardian | THE60B31S | 5 | Tons | 1900 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
11- 656138-1 | DX AHU | Direct Expansion Split System Air Handler | CU-11 | Guardian | THE60B31S | 5 | Tons | 1900 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
12- 701660-1 | VRF | Variable Refrigerant Flow | HP-N1 | Mitsubishi | PURY-P288TSKML | 24 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
12- 701660-1 | VRF | Variable Refrigerant Flow | HP-N2 | Mitsubishi | PURY-P192TSKML | 16 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
12- 701660-1 | VRF | Variable Refrigerant Flow | HP-S1 | Mitsubishi | PURY-P288TSKML | 24 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
12- 701660-1 | VRF | Variable Refrigerant Flow | HP-S2 | Mitsubishi | PURY-P192TSKML | 16 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-1 | Daikin | REYQ288TAYDU | 246 | Btu/hr |  |  | 11.7 | EER | 21.1 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-2 | Daikin | REYQ240TAYDU | 189 | Btu/hr |  |  | 12.2 | EER | 21.9 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-3 | Daikin | REYQ192TAYDU | 148 | Btu/hr |  |  | 12.5 | EER | 22.9 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-4 | Daikin | REYQ192TAYDU | 148 | Btu/hr |  |  | 12.5 | EER | 22.9 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-5 | Daikin | REYQ168TAYDU | 131 | Btu/hr |  |  | 11.6 | EER | 22 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-6 | Daikin | REYQ120TAYDU | 90 | Btu/hr |  |  | 13.1 | EER | 25.4 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-7 | Daikin | REYQ96TAYDU | 99 | Btu/hr |  |  | 14.3 | EER | 27.3 | IEER | Electric | N/A | Yes
13- 404186-1 | VRF | Variable Refrigerant Flow | HP-R-8 | Daikin | REYQ72TAYDU | 71 | Btu/hr |  |  | 14.8 | EER | 25.9 | IEER | Electric | N/A | Yes
13- 636582-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-1 | Carrier | 48P3L100 | 882.4 | MBH | 38520 | CFM | 9.5 | EER |  |  | Electric | Variable Volume (VAV) | N/A
13- 636582-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-2 | Carrier | 48P3L100 | 884.3 | MBH | 40000 | CFM | 9.5 | EER |  |  | Electric | Variable Volume (VAV) | N/A
13- 636582-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-3 | Trane | 4YCC3018 | 17 | MBH | 440 | CFM | 11 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
13- 636582-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-4 | Trane | 4YCC3018 | 17 | MBH | 440 | CFM | 11 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
14- 426751-1 | VRF | Variable Refrigerant Flow | HP-1A | Mitsubishi | PURY-P144TLMU | 144 | MBH |  |  | 21.9 | SEER | 21.9 | IEER | Electric | N/A | Yes
14- 426751-1 | VRF | Variable Refrigerant Flow | HP-1B | Mitsubishi | PURY-P144TLMU | 144 | MBH |  |  | 21.9 | SEER | 21.9 | IEER | Electric | N/A | Yes
14- 426751-1 | VRF | Variable Refrigerant Flow | CU-1 | Mitsubishi | PUY-A24NHA6 | 24 | MBH |  |  | 17 | SEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H1 | Daikin | REYQ456TYDN | 38 | Tons |  |  | 15.9 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H2 | Daikin | REYQ456TYDN | 38 | Tons |  |  | 15.9 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H3 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H4 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H5 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H6 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H7 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H8 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H9 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H10 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H11 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H12 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-H13 | Daikin | REYQ288TYDN | 24 | Tons |  |  | 18.2 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-L1 | Daikin | REYQ312TYDN | 26 | Tons |  |  | 17.8 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-L2 | Daikin | REYQ312TYDN | 26 | Tons |  |  | 17.8 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-L3 | Daikin | REYQ432TYDN | 36 | Tons |  |  | 16.5 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-L4 | Daikin | REYQ432TYDN | 36 | Tons |  |  | 16.5 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-L5 | Daikin | REYQ432TYDN | 36 | Tons |  |  | 16.5 | IEER |  |  | Electric | N/A | Yes
14- 493663-2 | VRF | Variable Refrigerant Flow | VRV-L6 | Daikin | REYQ432TYDN | 36 | Tons |  |  | 16.5 | IEER |  |  | Electric | N/A | Yes
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Lennox | KGB048S4D | 47500 | Btu/hr | 1500 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Lennox | KGB048S4D | 47500 | Btu/hr | 1450 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Lennox | KGB048S4D | 47500 | Btu/hr | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Lennox | KGB048S4D | 47500 | Btu/hr | 1650 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Lennox | KGB060S4D | 59500 | Btu/hr | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Lennox | KGB036S4D | 37200 | Btu/hr | 1150 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Lennox | KGA072S4B | 69000 | Btu/hr | 2475 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Lennox | KGB036S4D | 37200 | Btu/hr | 1225 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Lennox | KGB030S4D | 30200 | Btu/hr | 975 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Lennox | KGB060S4D | 59500 | Btu/hr | 1900 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Lennox | KGB036S4D | 37200 | Btu/hr | 1275 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-12 | Lennox | KGB060S4D | 59500 | Btu/hr | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-13 | Lennox | KGB036S4D | 37200 | Btu/hr | 1150 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-14 | Lennox | KGB030S4D | 30200 | Btu/hr | 1000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-15 | Lennox | KGB030S4D | 30200 | Btu/hr | 1000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 494803-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-16 | Lennox | KGB060S4D | 59500 | Btu/hr | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-1 | Mitsubishi | MXZ-8B48NA | 42 | MBH |  |  | 15 | SEER | 15 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-2 | Carrier | 25HCD330A005 | 24 | MBH |  |  | 13 | SEER | 13 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-3 | Carrier | 25HCD348A005 | 48 | MBH |  |  | 13 | SEER | 13 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-4 | Carrier | 25HCD330A005 | 30 | MBH |  |  | 13 | SEER | 13 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-5 | Carrier | 25HCD336A005 | 36 | MBH |  |  | 13 | SEER | 13 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-6 | Carrier | 25HCD336A005 | 36 | MBH |  |  | 13 | SEER | 13 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-7 | Mitsubishi | PUZ-A24NHA4 | 24 | MBH |  |  | 16 | SEER | 16 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-9 | Mitsubishi | PUZ-A24NHA4 | 24 | MBH |  |  | 13 | SEER | 13 | EER | Electric | N/A | N/A
14- 526453-1 [DHP] | DHP | Ductless Heat Pump | HP-10 | Mitsubishi | SUZ-KA15NA | 15 | MBH |  |  | 16 | SEER | 16 | EER | Electric | N/A | N/A
18- 595441 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-101 | Carrier | 48KC04 | 30.3 | MBH | 1200 | CFM | 14 | SEER | 12 | EER | Electric | Variable Volume (VAV) | N/A
18- 595441 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-102 | Carrier | 48KC04 | 30.3 | MBH | 1200 | CFM | 14 | SEER | 12 | EER | Electric | Variable Volume (VAV) | N/A
18- 595441 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-103 | Carrier | 48KC05 | 47.5 | MBH | 1600 | CFM | 14 | SEER | 12 | EER | Electric | Variable Volume (VAV) | N/A
18- 595441 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-104 | Carrier | 48KC05 | 47.5 | MBH | 1600 | CFM | 14 | SEER | 12 | EER | Electric | Variable Volume (VAV) | N/A
14- 540112-1 [Corridors\Main Floor Areas] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | AAON | RQ-004 | 55.4 | MBH | 1600 | CFM | 15.7 | SEER | 13.3 | EER | Electric | Variable Volume (VAV) | N/A
14- 540112-1 [Misc.] | DHP | Ductless Heat Pump | CU-1 | Daikin | RX18NMVJU | 18000 | Btu/hr |  |  | 18 | SEER | 12.5 | EER | Electric | N/A | N/A
14- 540112-1 [Misc.] | DHP | Ductless Heat Pump | CU-3 | Fujitsu | AOU30RLXB | 30000 | Btu/hr |  |  | 16.5 | SEER | 9.5 | EER | Electric | N/A | N/A
14- 540112-1 [Misc.] | DHP | Ductless Heat Pump | CU-4 | Daikin | RX18NMJVU | 18000 | Btu/hr |  |  | 18 | SEER | 12.5 | EER | Electric | N/A | N/A
14- 540112-1 [Misc.] | DHP | Ductless Heat Pump | CU-5 | Daikin | RX12NMJVU | 10900 | Btu/hr |  |  | 19 | SEER | 12.5 | EER | Electric | N/A | N/A
14- 540112-1 [Misc.] | DHP | Ductless Heat Pump | CU-6 | Daikin | RX12NMJVU | 10900 | Btu/hr |  |  | 19 | SEER | 12.5 | EER | Electric | N/A | N/A
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-C-W | Fujitsu | AQUA144TLCVG | 138 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-B-S | Fujitsu | AQUA168TLCVG | 160 | MBH |  |  | 11 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-B-NE | Fujitsu | AQUA192TLCVG | 184 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-B-E | Fujitsu | AQUA192TLCVG | 184 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-C-SW | Fujitsu | AQUA192TLCVG | 184 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-B-N | Fujitsu | AQUA192TLCVG | 184 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-D-E | Fujitsu | AQUA216TLCVG | 206 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-D-W | Fujitsu | AQUA216TLCVG | 206 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-NE | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-N | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-NW | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-W | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-SW | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-S | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 550027-2 | VRF | Variable Refrigerant Flow | VRF-A-SE | Fujitsu | A0UA96TLCV | 92 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
14- 673795-2 | VRF | Variable Refrigerant Flow | ACU-1 | Mitsubishi | PURY-P288TSLMU-A | 297 | MBH |  |  | 12.2 | SEER | N/A |  | Electric | N/A | Yes
14- 673795-2 | VRF | Variable Refrigerant Flow | ACU-2 | Mitsubishi | PURY-P288TSLMU-A | 297 | MBH |  |  | 12.2 | SEER | N/A |  | Electric | N/A | Yes
14- 673795-2 | VRF | Variable Refrigerant Flow | ACU-3 | Mitsubishi | PUMY-P36NHMU | 37.2 | MBH |  |  | 14.3 | SEER | N/A |  | Electric | N/A | Yes
14- 673795-2 | VRF | Variable Refrigerant Flow | ACU-4 | Mitsubishi | MUY-GE09NA | 9.5 | MBH |  |  | 24.6 | SEER | N/A |  | Electric | N/A | Yes
14- 587282-1 | VRF | Variable Refrigerant Flow | CU-1 | Daikin | REYQ216PBTJ | 206 | MBH |  |  | 17.2 | IEER | 16.4 | IEER | Electric | N/A | No
14- 587282-1 | VRF | Variable Refrigerant Flow | CU-2 | Daikin | REYQ192PBTJ | 184 | MBH |  |  | 18.7 | IEER | 16.9 | IEER | Electric | N/A | No
14- 587282-1 | VRF | Variable Refrigerant Flow | CU-3 | Daikin | REYQ216PBTJ | 206 | MBH |  |  | 17.2 | IEER | 16.4 | IEER | Electric | N/A | No
14- 626014-1 | DHP | Ductless Heat Pump | CU-1 | Mitsubishi | SUZ-KA15NA | 15 | MBH |  |  | 16 | SEER | 16 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-4 | Mitsubishi | MUZ-GE09NA | 9 | MBH |  |  | 26 | SEER | 26 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-5 | Mitsubishi | PUZ-A24NHA4 | 42 | MBH |  |  | 17 | SEER | 17 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-6 | Mitsubishi | PUZ-A30NHA4 | 12 | MBH |  |  | 15.2 | SEER | 15.2 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-7 | Mitsubishi | PUZ-HA36NHA4 | 35 | MBH |  |  | 15 | SEER | 15 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-8 | Mitsubishi | PUZ-HA42NKA | 42 | MBH |  |  | 13.8 | SEER | 13.8 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-9 | Mitsubishi | SUZ-KA09NA | 10.9 | MBH |  |  | 15 | SEER | 15 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-10 | Mitsubishi | SUZ-KA12NA | 11.5 | MBH |  |  | 16 | SEER | 16 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-11 | Mitsubishi | SUZ-KA15NA | 14.1 | MBH |  |  | 15.5 | SEER | 15.5 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-12 | Mitsubishi | SUZ-KA18NA | 17.2 | MBH |  |  | 17.5 | SEER | 17.5 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-15 | Mitsubishi | PUZ-A18NHA4 | 18 | MBH |  |  | 14.3 | SEER | 14.3 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-16 | Mitsubishi | MXZ-3C24NA | 14.1 | MBH |  |  | 16 | SEER | 16 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-17 | Mitsubishi | MXZ-5C42NAHZ | 11.5 | MBH |  |  | 16 | SEER | 16 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-18 | Mitsubishi | PUZ-A12NHA4 | 14.1 | MBH |  |  | 15.5 | SEER | 15.5 | IEER | Electric | N/A | N/A
14- 626014-1 | DHP | Ductless Heat Pump | CU-19 | Mitsubishi | PUMY-P60NKMU | 17.2 | MBH |  |  | 16.7 | SEER | 16.7 | IEER | Electric | N/A | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#1 | Lennox | LGH120H4BM-G | 124400 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#2 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#3 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#4 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#5 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#6 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#7 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#8 | Lennox | LGH060H4EM-G | 63200 | Btu/hr | 2000 | CFM | 12.7 | EER | 17 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#9 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#10 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#11 | Lennox | LGH092H4BM-G | 93000 | Btu/hr | 3000 | CFM | 12.5 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
14- 634379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#12 | Lennox | LGH036H4EM-G | 35800 | Btu/hr | 1200 | CFM | 21.5 | EER | 17 | IEER | Electric | Constant Volume (CV) | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-21 | Trane | YHC036 | 38 | MBH | 1200 | CFM | 15.2 | SEER |  |  | Electric | 2-Speed | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-22 | Trane | YHC036 | 38 | MBH | 1200 | CFM | 15.2 | SEER |  |  | Electric | 2-Speed | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-23 | Trane | YHC036 | 38 | MBH | 1200 | CFM | 15.2 | SEER |  |  | Electric | 2-Speed | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-24 | Trane | YHC120 | 119 | MBH | 4000 | CFM | 14.7 | IEER |  |  | Electric | Variable Volume (VAV) | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-25 | Trane | YHD150 | 149 | MBH | 5000 | CFM | 12.1 | EER |  |  | Electric | Variable Volume (VAV) | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-26 | Trane | YHD150 | 149 | MBH | 5000 | CFM | 12.1 | EER |  |  | Electric | Variable Volume (VAV) | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-27 | Trane | YHC036 | 38 | MBH | 1200 | CFM | 15.2 | SEER |  |  | Electric | 2-Speed | N/A
14- 662676-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC-28 | Trane | YHC036 | 38 | MBH | 1200 | CFM | 15.2 | SEER |  |  | Electric | 2-Speed | N/A
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.00 | Mitsubishi | PURY-P264YSKMU-A | 264 | MBH |  |  | 11 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.01 | Mitsubishi | PURY-P264YSKMU-A | 264 | MBH |  |  | 11 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.02 | Mitsubishi | PURY-P288YSKMU-A | 288 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.03 | Mitsubishi | PURY-P288YSKMU-A | 288 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.04 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.05 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.06 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.07 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.08 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R1.09 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | Yes
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.00 | Mitsubishi | PURY-P264YSKMU-A | 264 | MBH |  |  | 11 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.01 | Mitsubishi | PURY-P264YSKMU-A | 264 | MBH |  |  | 11 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.03 | Mitsubishi | PURY-P288YSKMU-A | 288 | MBH |  |  | 11.2 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.04 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.05 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.06 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.07 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.08 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R2.09 | Mitsubishi | PURY-P216YSKMU-A | 216 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.00 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.01 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.02 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.03 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.04 | Mitsubishi | PURY-P240YSKMU-A | 240 | MBH |  |  | 10.9 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.05 | Mitsubishi | PURY-P168YSKMU-A | 168 | MBH |  |  | 12.1 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.06 | Mitsubishi | PURY-P168YSKMU-A | 168 | MBH |  |  | 12.1 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.07 | Mitsubishi | PURY-P168YSKMU-A | 168 | MBH |  |  | 12.1 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.08 | Mitsubishi | PURY-P168YSKMU-A | 168 | MBH |  |  | 12.1 | EER |  |  | Electric | N/A | No
14- 668269-1 | VRF | Variable Refrigerant Flow | R3.09 | Mitsubishi | PURY-P168YSKMU-A | 168 | MBH |  |  | 12.1 | EER |  |  | Electric | N/A | No
14- 731874-1 [RTU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Daikin | MPSH15B | 174.1 | MBH | 6000 | CFM | 12.2 | EER | N/A |  | Electric | Constant Volume (CV) | N/A
14- 731874-1 [VRF] | VRF | Variable Refrigerant Flow | HP-1 | Daikin | REYQ168TYDN | 131.8 | MBH |  |  | 11.3 | EER | 19.5 | IEER | Electric | N/A | Yes
14- 731874-1 [VRF] | VRF | Variable Refrigerant Flow | HP-2 | Daikin | REYQ72TYDN | 56 | MBH |  |  | 13.4 | EER | 20.8 | IEER | Electric | N/A | Yes
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 1 | Unknown | Unknown | 20 | Tons | 6500 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 2 | Unknown | Unknown | 10 | Tons | 3700 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 3 | Unknown | Unknown | 5 | Tons | 1650 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 4 | Unknown | Unknown | 5 | Tons | 1200 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 5 | Unknown | Unknown | 5 | Tons | 1200 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 6 | Unknown | Unknown | 5 | Tons | 9000 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 7 | Unknown | Unknown | 5 | Tons | 9000 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 8 | Unknown | Unknown | 3 | Tons | 9000 | CFM | 14.3 | EER | 15.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 9 | Unknown | Unknown | 3 | Tons | 6500 | CFM | 14.3 | EER | 15.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 10 | Unknown | Unknown | 10 | Tons | 4800 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 11 | Unknown | Unknown | 5 | Tons | 8000 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 12 | Unknown | Unknown | 3 | Tons | 3700 | CFM | 14.3 | EER | 15.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 13 | Unknown | Unknown | 3 | Tons | 8000 | CFM | 14.3 | EER | 15.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 14 | Unknown | Unknown | 20 | Tons | 4500 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 15 | Unknown | Unknown | 20 | Tons | 9000 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 16 | Unknown | Unknown | 20 | Tons | 9000 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 17 | Unknown | Unknown | 20 | Tons | 1200 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 18 | Unknown | Unknown | 10 | Tons | 3700 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 19 | Unknown | Unknown | 20 | Tons | 3700 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 20 | Unknown | Unknown | 20 | Tons | 3700 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 21 | Unknown | Unknown | 10 | Tons | 1650 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 22 | Unknown | Unknown | 20 | Tons | 1650 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 23 | Unknown | Unknown | 20 | Tons | 1650 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 24 | Unknown | Unknown | 3 | Tons | 6000 | CFM | 14.3 | EER | 15.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 25 | Unknown | Unknown | 10 | Tons | 6000 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 26 | Unknown | Unknown | 10 | Tons | 1650 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 27 | Unknown | Unknown | 10 | Tons | 1650 | CFM | 12.1 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 28 | Unknown | Unknown | 5 | Tons | 1650 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 29 | Unknown | Unknown | 5 | Tons | 1650 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 30 | Unknown | Unknown | 20 | Tons | 1650 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 31 | Unknown | Unknown | 20 | Tons | 1200 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 411092-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 32 | Unknown | Unknown | 5 | Tons | 1200 | CFM | 12.8 | EER | 15.5 | SEER | Electric | Constant Volume (CV) | N/A
15- 419460-1 | VRF | Variable Refrigerant Flow | CU-1a | Mitsubishi | PURY-192TSLMU | 96 | MBH |  |  | 23.5 | IEER |  |  | Electric | N/A | Yes
15- 419460-1 | VRF | Variable Refrigerant Flow | CU-1b | Mitsubishi | PURY-192TSLMU | 96 | MBH |  |  | 23.5 | IEER |  |  | Electric | N/A | Yes
15- 419460-1 | VRF | Variable Refrigerant Flow | CU-2 | Mitsubishi | MXZ-8C48NA | 48 | MBH |  |  | 18.9 | SEER |  |  | Electric | N/A | Yes
15- 419460-1 | VRF | Variable Refrigerant Flow | CU-3 | Mitsubishi | MXZ-8C48NA | 48 | MBH |  |  | 18.9 | SEER |  |  | Electric | N/A | Yes
15- 425673-1 | VRF | Variable Refrigerant Flow | HP-1 | MITSUBISHI | PURY | 120 | MBH |  |  | 11.7 | EER |  |  | Electric | N/A | Yes
15- 425673-1 | VRF | Variable Refrigerant Flow | HP-2 | MITSUBISHI | PURY | 72 | MBH |  |  | 13.5 | EER |  |  | Electric | N/A | Yes
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48KC06 | 45630 | Btu/hr | 2000 | CFM | 14.1 | SEER | 12 | EER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48TC09 | 77220 | Btu/hr | 3400 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48TC24 | 188760 | Btu/hr | 8000 | CFM | 9.8 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Carrier | 48KC04 | 27612 | Btu/hr | 1200 | CFM | 14 | SEER | 12 | EER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Carrier | 48KC04 | 27612 | Btu/hr | 1200 | CFM | 14 | SEER | 12 | EER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Carrier | 48TC08 | 68640 | Btu/hr | 3000 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Carrier | 48KC05 | 37050 | Btu/hr | 1600 | CFM | 14 | SEER | 12 | EER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Carrier | 48TC07 | 54600 | Btu/hr | 2400 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Carrier | 48KC06 | 45630 | Btu/hr | 2000 | CFM | 12 | EER | 14.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Carrier | 48TC17 | 157560 | Btu/hr | 6000 | CFM | 10.8 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Carrier | 48TC17 | 157560 | Btu/hr | 6000 | CFM | 10.8 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-12 | Carrier | 48KC06 | 45630 | Btu/hr | 2000 | CFM | 12 | EER | 14.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-13 | Carrier | 48KC05 | 37050 | Btu/hr | 1600 | CFM | 12 | EER | 14 | SEER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-14 | Carrier | 48TC07 | 54600 | Btu/hr | 2400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-15 | Carrier | 48KC06 | 45630 | Btu/hr | 2000 | CFM | 12 | EER | 14.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 427602-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-16 | Carrier | 48KC06 | 45630 | Btu/hr | 2000 | CFM | 12 | EER | 14.1 | SEER | Electric | Constant Volume (CV) | N/A
15- 458201-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Aaon | RQ | 36 | MBH | 1200 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
15- 458201-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Aaon | RQ | 48 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
15- 458201-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Aaon | RN | 150 | MBH | 5000 | CFM | 11 | EER |  |  | Electric | Variable Volume (VAV) | N/A
15- 458201-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Aaon | RN | 162 | MBH | 5400 | CFM | 11 | EER |  |  | Electric | Variable Volume (VAV) | N/A
15- 458201-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Aaon | RN | 150 | MBH | 5000 | CFM | 11 | EER |  |  | Electric | Variable Volume (VAV) | N/A
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-2A | Daikin | REYQ168TTJU | 312000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-2B | Daikin | N/A | 134000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-3A | Daikin | N/A | 156000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-3B | Daikin | N/A | 134000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-4A | Daikin | N/A | 134000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-4B | Daikin | N/A | 134000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-5A | Daikin | N/A | 134000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-5B | Daikin | N/A | 134000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-6A | Daikin | N/A | 156000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-6B | Daikin | N/A | 156000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 464466-1 | VRF | Variable Refrigerant Flow | HRU-A1 | Daikin | REYQ264TTJU | 232699 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | York | XP060C00B2C1AAA1A1 | 5 | Tons | 740 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | York | XP060C00B2C1AAA1A1 | 5 | Tons | 785 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | York | XP060C00B2C1AAA1A1 | 5 | Tons | 510 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | York | XP060C00B2C1AAA1A1 | 5 | Tons | 360 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | York | XP060C00B2C1AAA1A1 | 5 | Tons | 400 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-6 | York | XP060C00B2C1AAA1A1 | 5 | Tons | 470 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
14- 526453-1 [RTU] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-7 | York | XP048C00B2C1AAA1A1 | 4 | Tons | 335 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
15- 527020-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Carrier | 48HCFA06 | 54 | MBH | 2000 | CFM | 15.2 | SEER |  |  | Electric | Constant Volume (CV) | N/A
15- 580950-1 | VRF | Variable Refrigerant Flow | ACU-R-X-1 | LG | ARUB096DTE4 | 96000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Unknown
15- 580950-1 | VRF | Variable Refrigerant Flow | ACU-R-X-2 | LG | ARUB096DTE4 | 240000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Unknown
15- 580950-1 | VRF | Variable Refrigerant Flow | ACU-R-X-3 | LG | ARUB216DTE4 | 216000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Unknown
15- 580950-1 | VRF | Variable Refrigerant Flow | ACU-R-X-4 | LG | ARUB264DTE4 | 264000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Unknown
15- 580950-1 | VRF | Variable Refrigerant Flow | ACU-R-X-5 | LG | ARUB360DTE4 | 360000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Unknown
15- 580950-1 | VRF | Variable Refrigerant Flow | ACU-R-X-6 | LG | ARUB168DTE4 | 168000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Unknown
15- 589031-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YHD180F3RHA | 152.81 | MBH | 6000 | CFM | 12 | EER |  |  | Electric | Variable Volume (VAV) | N/A
15- 589031-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YHD300F3RHA | 242.36 | MBH | 9500 | CFM | 10.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
15- 602446-1 | VRF | Variable Refrigerant Flow | CU-1 | Mitsubishi | PURY-HP192TSKMU-A-H | 192000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 602446-1 | VRF | Variable Refrigerant Flow | CU-2 | Mitsubishi | PURY-HP192TSKMU-A-H | 192000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 602446-1 | VRF | Variable Refrigerant Flow | CU-3 | Mitsubishi | PURY-HP192TSKMU-A-H | 192000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 602446-1 | VRF | Variable Refrigerant Flow | CU-4 | Mitsubishi | PUZ-A18NHA3 | 18000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 602446-1 | VRF | Variable Refrigerant Flow | CU-5 | Mitsubishi | PURY-HP96TSKMU-A-H | 96000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
03- 779006-1 | VRF | Variable Refrigerant Flow | HP-1 | Daikin | REYQ120TYDN | 102 | MBH |  |  | 10.8 | EER | 20.7 | IEER | Electric | N/A | Yes
15- 692220-1 | DHP | Ductless Heat Pump | HP-1 | LG | ARUN038GSS4 | 38 | MBH |  |  | 11 | EER |  |  | Electric | N/A | N/A
15- 692220-1 | DHP | Ductless Heat Pump | HP-2 | LG | LUU247 | 24 | MBH |  |  | 12 | EER |  |  | Electric | N/A | N/A
15- 692220-1 | DHP | Ductless Heat Pump | HP-3 | LG | LUU187HV | 19.8 | MBH |  |  | 15 | EER |  |  | Electric | N/A | N/A
15- 692220-1 | DHP | Ductless Heat Pump | HP-5 | LG | LSU180HSV | 18.2 | MBH |  |  | 12.6 | EER |  |  | Electric | N/A | N/A
15- 692220-1 | DHP | Ductless Heat Pump | HP-7 | LG | LSU180HSV | 18.2 | MBH |  |  | 12.6 | EER |  |  | Electric | N/A | N/A
15- 692220-1 | DHP | Ductless Heat Pump | HP-4 | LG | LSU240HEV1 | 24 | MBH |  |  | 10.76 | EER |  |  | Electric | N/A | N/A
15- 692220-1 | DHP | Ductless Heat Pump | HP-6 | LG | LSU180HSV | 22 | MBH |  |  | 12.6 | EER |  |  | Electric | N/A | N/A
15- 700290-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-1 | Carrier | 48TCD012 | 88.6 | MBH | 4000 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 700290-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-2 | Carrier | 48TCD014 | 105 | MBH | 4800 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 700290-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-3 | Carrier | 48TCD06 | 43.1 | MBH | 1950 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
15- 700290-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-4 | Carrier | 48TCD05 | 32.9 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 400924-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | AAON | RN050 | 444.1 | MBH | 19400 | CFM | 11 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 400924-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | AAON | RN050 | 441.5 | MBH | 19400 | CFM | 11 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 400924-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | AAON | RN050 | 441.63 | MBH | 19400 | CFM | 11 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 400924-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | AAON | RN026 | 221.9 | MBH | 10650 | CFM | 11.4 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 403736-1 | VRF | Variable Refrigerant Flow | HP-1 | Trane | TUHYP072AN40A(N/B) | 72000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | No
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-3 | Carrier | 59SC08016 | 42 | MBH | 1400 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-4 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-5 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-6 | Carrier | 59SC06010 | 31.6 | MBH | 1200 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-7 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-8 | Carrier | 59SC08016 | 42 | MBH | 1600 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-9 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-10 | Carrier | 59SC06010 | 31.6 | MBH | 1200 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-11 | Carrier | 59SC06010 | 31.6 | MBH | 1200 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-12 | Carrier | 59SC06010 | 31.6 | MBH | 1200 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-13 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-14 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-15 | Carrier | 59SC08016 | 42 | MBH | 1600 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 404663-1 | DX AHU | Direct Expansion Split System Air Handler | F-16 | Carrier | 59SC12020 | 53 | MBH | 1800 | CFM | Unknown |  | Unknown |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Unknown | Unknown | 218 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Unknown | Unknown | 218 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Unknown | Unknown | 180 | MBH | 7000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Unknown | Unknown | 180 | MBH | 7000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Unknown | Unknown | 84 | MBH | 3000 | CFM | 12.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Unknown | Unknown | 280 | MBH | 10000 | CFM | 11.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Unknown | Unknown | 280 | MBH | 10000 | CFM | 11.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Unknown | Unknown | 218 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Unknown | Unknown | 218 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 412293-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Unknown | Unknown | 218 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
14- 611061-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2B | Carrier | 25HHA436 | 3 | Tons |  |  | 14 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
14- 611061-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3B | Carrier | 25HHA448 | 4 | Tons |  |  | 14 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
14- 611061-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4B | Carrier | 25HHA448 | 4 | Tons |  |  | 14 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | YORK | XP060C00B2C1AAA1A1 | 5 | Tons | 1995 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | YORK | XP060C00B2C1AAA1A1 | 5 | Tons | 1975 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | YORK | XP060C00B2C1AAA1A1 | 5 | Tons | 1860 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 427879-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | PAC-A04 | Carrier | 48TCE-A005 | 45 | MBH | 1840 | CFM | 13 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 427879-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | PAC-A08 | Carrier | 48TCE-A005 | 45 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 427879-1 | DX AHU | Direct Expansion Split System Air Handler | AHU-A01 | Carrier | 38AUD016 | 182.7 | MBH | 5440 | CFM | 13 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 427879-1 | DX AHU | Direct Expansion Split System Air Handler | AHU-A02 | Carrier | 38AUD016 | 182.7 | MBH | 5300 | CFM | 13 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 427879-1 | DX AHU | Direct Expansion Split System Air Handler | AHU-A03 | Carrier | 24ABB3-60 | 58.1 | MBH | 2040 | CFM | 13.5 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 427879-1 | DX AHU | Direct Expansion Split System Air Handler | AHU-A04 | Carrier | 24ABB3-60 | 46.9 | MBH | 1630 | CFM | 14.5 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 438381-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HVAC-1 | Trane | YSH240F3RLA | 41200 | Btu/hr | 8000 | CFM | 10 | EER | 14 | SEER | Electric | Variable Volume (VAV) | N/A
16- 438381-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HVAC-2 | Trane | YSH240F3RLA | 41200 | Btu/hr | 8000 | CFM | 10 | EER | 14 | SEER | Electric | Variable Volume (VAV) | N/A
16- 490400-1 | VRF | Variable Refrigerant Flow | HP-1 | Mitsubishi | PURY-HP96TKMU-A-H | 96000 | Btu/hr |  |  | 12.5 | EER |  |  | Electric | N/A | Yes
14- 730160-1 | VRF | Variable Refrigerant Flow | HP 1N | Daikin | REYQ288TYDN | 215.3 | MBH |  |  | 11.8 | EER |  |  | Electric | N/A | Yes
14- 730160-1 | VRF | Variable Refrigerant Flow | HP 1S | Daikin | REYQ336TYDN | 261.1 | MBH |  |  | 10.7 | EER |  |  | Electric | N/A | Yes
14- 730160-1 | VRF | Variable Refrigerant Flow | HP 2 | Daikin | REYQ408TYDN | 314 | MBH |  |  | 9.8 | EER |  |  | Electric | N/A | Yes
14- 730160-1 | VRF | Variable Refrigerant Flow | HP 3 | Daikin | REYQ456TYDN | 363.2 | MBH |  |  | 9.5 | EER |  |  | Electric | N/A | Yes
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | DX AHU | Direct Expansion Split System Air Handler | AHU-1 | York | 51X63 | 167.1 | MBH | 7200 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | DX AHU | Direct Expansion Split System Air Handler | AHU-2 | York | 45X54 | 126.2 | MBH | 5175 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
15- 419203-1 [Additional Areas] | VRF | Variable Refrigerant Flow | OHP-1 | Daikin | REYQ360PBTJ | 342000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 419203-1 [Additional Areas] | VRF | Variable Refrigerant Flow | OHP-2 | Daikin | REYQ360PBTJ | 342000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 419203-1 [Additional Areas] | VRF | Variable Refrigerant Flow | OHP-3 | Daikin | REYQ360PBTJ | 342000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
15- 419203-1 [Additional Areas] | VRF | Variable Refrigerant Flow | OHP-4 | Daikin | REYQ360PBTJ | 342000 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
16- 514976-1 | VRF | Variable Refrigerant Flow | HP1 | Daikin | REYQ168TTJU | 168000 | Btu/hr |  |  | 19.5 | EER |  | SEER | Electric | N/A | No
16- 514976-1 | VRF | Variable Refrigerant Flow | HP4 | Daikin | REYQ96TTJU | 96000 | Btu/hr |  |  | 29.3 | EER |  | SEER | Electric | N/A | No
16- 514976-1 | VRF | Variable Refrigerant Flow | HP3 | Daikin | REYQ96TTJU | 48000 | Btu/hr |  |  | 18.8 | EER |  | SEER | Electric | N/A | No
16- 514976-1 | VRF | Variable Refrigerant Flow | HP5 | Daikin | RXN12NMVJU | 12000 | Btu/hr |  |  | 15 | EER |  | SEER | Electric | N/A | No
16- 536718-1 | VRF | Variable Refrigerant Flow | VRF-A | Daikin | REYQ168TATJU | 162 | MBH |  |  | 11.6 | EER | 22 | IEER | Electric | N/A | Yes
16- 536718-1 | VRF | Variable Refrigerant Flow | VRF-B | Daikin | REYQ168TATJU | 165 | MBH |  |  | 11.6 | EER | 22 | IEER | Electric | N/A | Yes
16- 536718-1 | VRF | Variable Refrigerant Flow | VRF-C | Daikin | REYQ96TATJU | 90 | MBH |  |  | 14.6 | EER | 29.3 | IEER | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-1 | LG | ARUM336 | 336 | MBH |  |  | 20.5 | IEER |  |  | Electric | N/A | No
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-2 | LG | ARUB384 | 432 | MBH |  |  | 19.3 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-3 | LG | ARUM096 | 96 | MBH |  |  | 23.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-4 | LG | ARUM096 | 96 | MBH |  |  | 23.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-5 | LG | ARUB120 | 120 | MBH |  |  | 24.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-6 | LG | ARUM096 | 96 | MBH |  |  | 23.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-7 | LG | ARUM096 | 96 | MBH |  |  | 23.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-8 | LG | ARUB120 | 120 | MBH |  |  | 24.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-9 | LG | ARUB384 | 384 | MBH |  |  | 19.3 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-10 | LG | ARUB384 | 384 | MBH |  |  | 19.3 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-11 | LG | ARUM336 | 336 | MBH |  |  | 20.5 | IEER |  |  | Electric | N/A | No
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-12 | LG | ARUM096 | 96 | MBH |  |  | 23.6 | IEER |  |  | Electric | N/A | Yes
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-13 | LG | ARUN168 | 168 | MBH |  |  | 21.9 | IEER |  |  | Electric | N/A | No
16- 537171-1 | VRF | Variable Refrigerant Flow | CU R-14 | LG | ARUN168 | 168 | MBH |  |  | 21.9 | IEER |  |  | Electric | N/A | No
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | YORK | XP060C00B2C1AAA1A1 | 5 | Tons | 1860 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | YORK | XP060C00B2C1AAA1A1 | 5 | Tons | 1950 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-6 | YORK | XP060C00B2C1AAA1A1 | 5 | Tons | 1840 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 572659-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48TC08 | 75.61 | MBH | 3000 | CFM | 11 | EER |  |  | Electric | Unknown | N/A
16- 577162-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48TCEA05 | 34.1 | MBH | 1600 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 577162-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48TCEA05 | 34.1 | MBH | 1600 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 577162-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48TCEA05 | 34.1 | MBH | 1600 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 577162-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Carrier | 48TCEA05 | 34.1 | MBH | 1600 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 607207-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48FC06 | 53.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 607207-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48FC06 | 53.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Unknown | N/A
16- 607207-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Carrier | 48FC04 | 30.9 | MBH | 1200 | CFM | 14 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
16- 607207-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48HC11 | 112 | MBH | 4000 | CFM | 12 | EER |  |  | Electric | Variable Volume (VAV) | N/A
15- 472299-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-7 | YORK | XP048C00B2C1AAA1A1 | 4 | Tons | 1560 | CFM | 13 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 423218-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Daikin | MHS007B | 88.9 | MBH | 2600 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 423218-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Daikin | MHSH03B | 35.1 | MBH | 1200 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 423218-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Daikin | MHSH03B | 35.1 | MBH | 1200 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 621440-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Daikin | DSG0360454BXXX | 35 | MBH | 1200 | CFM | 12 | EER | 14 | SEER | Electric | Constant Volume (CV) | N/A
16- 621440-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Daikin | DSG0490904BXXX | 47 | MBH | 1600 | CFM | 11.8 | EER | 14 | SEER | Electric | Constant Volume (CV) | N/A
16- 640402-1 | DHP | Ductless Heat Pump | HP-1 | Mitsubishi | PUZ-A12NKA7-BS | 12 | MBH |  |  | 14 | SEER |  |  | Electric | N/A | N/A
16- 640402-1 | DHP | Ductless Heat Pump | HP-3 | Mitsubishi | MUZ-GL18NA-U1 | 18 | MBH |  |  | 20.5 | SEER |  |  | Electric | N/A | N/A
16- 640402-1 | DHP | Ductless Heat Pump | HP-9 | Mitsubishi | MUZ-HM09NA2-U8 | 9 | MBH |  |  | 18 | SEER |  |  | Electric | N/A | N/A
16- 640402-1 | DHP | Ductless Heat Pump | HP-12 | Mitsubishi | PUZ-A12NKA7-BS | 12 | MBH |  |  | 20.8 | SEER |  |  | Electric | N/A | N/A
16- 640402-1 | DHP | Ductless Heat Pump | HP-18 | Mitsubishi | MUZ-GL18NA-U1 | 18 | MBH |  |  | 20.5 | SEER |  |  | Electric | N/A | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48HC-09 | 64 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48HC-11 | 97 | MBH | 6000 | CFM | 12.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3A | Carrier | 48HC-08 | 68 | MBH | 3000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3B | Carrier | 48HC-08 | 68 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4A | Carrier | 48HC-08 | 68 | MBH | 3000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4B | Carrier | 48HC-12 | 93 | MBH | 4000 | CFM | 11.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4C | Carrier | 48HC-14 | 97 | MBH | 6000 | CFM | 12.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5A | Carrier | 48HC-09 | 68 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5B | Carrier | 48HC-09 | 68 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Carrier | 48HC-09 | 64 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Carrier | 48HC-14 | 97 | MBH | 6000 | CFM | 12.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Carrier | 48HC-14 | 97 | MBH | 6000 | CFM | 12.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Carrier | 48HC-09 | 64 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Carrier | 48HC-12 | 93 | MBH | 4000 | CFM | 11.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Carrier | 48HC-08 | 58 | MBH | 3160 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-12 | Carrier | 48HC-20 | 168 | MBH | 7000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-13 | Carrier | 48HC-08 | 58 | MBH | 2650 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
15- 573278-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-14 | Carrier | 48HC-17 | 144 | MBH | 6760 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 657491-1 | VRF | Variable Refrigerant Flow | MS1 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.9 | SEER | N/A |  | Electric | N/A | No
16- 657491-1 | VRF | Variable Refrigerant Flow | MS2 | Daikin | FXYMQ48PVJU | 47.5 | MBH |  |  | 15.1 | SEER | N/A |  | Electric | N/A | No
16- 423218-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Daikin | MHSH03B | 33.5 | MBH | 1050 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 423218-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | Daikin | MHSH03B | 33.5 | MBH | 1050 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 423218-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-6 | Daikin | MHSH03B | 33.5 | MBH | 1050 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 558605-2 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-C100-1 | LG | ARUN048GSS4 | 48000 | Btu/hr | 1500 | CFM | 10.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 680124-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Johnson Controls | J25ZIN30P4B5BCA2C1 | 294.8 | MBH | 10000 | CFM | 10.6 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
16- 680124-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Johnson Controls | J25ZIN30P4B5BCA2C1 | 294.8 | MBH | 10000 | CFM | 10.6 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
16- 680124-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Johnson Controls | J25ZIN30P4B5BCA2C1 | 294.8 | MBH | 10000 | CFM | 10.6 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
16- 680124-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Johnson Controls | JA3IN06B4B5BCA2A1 | 23.2 | MBH | 900 | CFM | 12.2 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
16- 680124-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Johnson Controls | JZ4ZIN06B4B5BCA2AI | 51.3 | MBH | 2000 | CFM | 12.2 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
16- 680124-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Johnson Controls | J12ZIN18R4B5BCA2AI | 164.5 | MBH | 5000 | CFM | 12 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
16- 688717-1 [RTU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48KCEA06 | 56 | MBH | 2000 | CFM | 14.1 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
16- 688717-1 [RTU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48KCEA06 | 56 | MBH | 2000 | CFM | 14.1 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
16- 688717-1 [RTU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48KCEA06 | 56 | MBH | 2000 | CFM | 14.1 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
16- 688717-1 [VRF] | VRF | Variable Refrigerant Flow | ODU-1 | LG | ARUM168BTE5 | 143.6 | MBH |  |  | 11.1 | EER | 21.9 | IEER | Electric | N/A | Yes
16- 706094-1 | VRF | Variable Refrigerant Flow | ACCU-701 | LG | ARUM336BTE5 | 336000 | Btu/hr |  |  | 19 | SEER |  |  | Electric | N/A | Yes
16- 706094-1 | VRF | Variable Refrigerant Flow | ACCU-702 | LG | ARUM312BTE5 | 312000 | Btu/hr |  |  | 20.2 | SEER |  |  | Electric | N/A | Yes
16- 706094-1 | VRF | Variable Refrigerant Flow | ACCU-703 | LG | ARUM408BTE5 | 408000 | Btu/hr |  |  | 17.2 | SEER |  |  | Electric | N/A | Yes
16- 706094-1 | VRF | Variable Refrigerant Flow | ACCU-704 | LG | ARUM288BTE5 | 288000 | Btu/hr |  |  | 21.1 | SEER |  |  | Electric | N/A | Yes
16- 706094-1 | VRF | Variable Refrigerant Flow | ACCU-705 | LG | ARUM336BTE5 | 336000 | Btu/hr |  |  | 19 | SEER |  |  | Electric | N/A | Yes
16- 720532-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#1 | Lennox | LRP16GE | 294.5 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 720532-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#2 | Lennox | LRP16GE | 124.4 | MBH | 4000 | CFM | 12 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 720532-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#3 | Lennox | LRP14GE | 147.6 | MBH | 5000 | CFM | 11 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 720532-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#4 | Lennox | LRP14GE | 63.3 | MBH | 1800 | CFM | 17.1 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-1 | Mitsubishi | PUMY-P48NKMU1 | 48 | MBH |  |  | 16.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-2 | Mitsubishi | PUZ-A36NHA6 | 36 | MBH |  |  | 15 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-3 | Mitsubishi | PUMY-P36NKMU1 | 30 | MBH |  |  | 15.6 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-4 | Mitsubishi | PUMY-P48NKMU1 | 48 | MBH |  |  | 16.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-5 | Mitsubishi | PUMY-P36NKMU1 | 24 | MBH |  |  | 15.6 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-6 | Mitsubishi | PUZ-A30NHA6 | 30 | MBH |  |  | 15.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-7 | Mitsubishi | PUMY-P48NKMU1 | 48 | MBH |  |  | 16.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-8 | Mitsubishi | PUZ-A24NHA6 | 24 | MBH |  |  | 16 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-9 | Mitsubishi | PUZ-A30NHA6 | 30 | MBH |  |  | 15.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-10 | Mitsubishi | PUZ-A36NHA6 | 36 | MBH |  |  | 15 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-11 | Mitsubishi | PUMY-P48NKMU1 | 48 | MBH |  |  | 16.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-12 | Mitsubishi | PUZ-A36NHA6 | 36 | MBH |  |  | 15 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-13 | Mitsubishi | PUMY-P48NKMU1 | 48 | MBH |  |  | 16.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-14 | Mitsubishi | PUMY-P48NKMU1 | 48 | MBH |  |  | 16.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-15 | Mitsubishi | MXZ-4C24NA | 24 | MBH |  |  | 18 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-16 | Mitsubishi | MXZ-3C30NA | 30 | MBH |  |  | 17.6 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-17 | Mitsubishi | PUZ-A36NHA6 | 36 | MBH |  |  | 15 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-18 | Mitsubishi | PUZ-A30NHA6 | 30 | MBH |  |  | 15.5 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-19 | Mitsubishi | MXZ-4C24NA | 24 | MBH |  |  | 18 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-20 | Mitsubishi | MXZ-4C24NA | 30 | MBH |  |  | 17.6 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-21 | Mitsubishi | PUZ-A36NHA6 | 36 | MBH |  |  | 15 | SEER |  |  | Electric | N/A | N/A
16- 727455-1 | DHP | Ductless Heat Pump | HP-22 | Mitsubishi | MXZ-4C24NA | 24 | MBH |  |  | 18 | SEER |  |  | Electric | N/A | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-1 | Carrier | 24ACB7 | 5 | Tons | 2115 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-2 | Carrier | 24ACB7 | 3 | Tons | 1425 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-3 | Carrier | 24ACB7 | 5 | Tons | 2005 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-4 | Carrier | 24ACB7 | 2 | Tons | 1175 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-5 | Carrier | 24ACB7 | 5 | Tons | 2000 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-6 | Carrier | 24ACB7 | 5 | Tons | 1980 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Common Areas and Corridors] | DX AHU | Direct Expansion Split System Air Handler | CU-7 | Carrier | 24ACB7 | 5 | Tons | 2000 | CFM | 17 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-1 | Daikin | RXYMQ48PVJU | 48 | MBH |  |  | 13.2 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-2 | Daikin | RXYMQ48PVJU | 48 | MBH |  |  | 13.2 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-3 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.4 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-4 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.4 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-5 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.4 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-7 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.4 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-8 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.4 | SEER | N/A |  | Electric | N/A | Yes
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-9 | Daikin | RXYMQ36PVJU | 36 | MBH |  |  | 14.4 | SEER | N/A |  | Electric | N/A | No
15- 640275-1 [Residences] | VRF | Variable Refrigerant Flow | HP-6 | Daikin | RXYMQ48PVJU | 48 | MBH |  |  | 13.2 | SEER | N/A |  | Electric | N/A | Yes
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Daikin | MPSH03C | 3 | Tons | 1100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Daikin | MPSH04C | 4 | Tons | 1300 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Daikin | MPSH05C | 5 | Tons | 1600 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Daikin | MPSH03C | 3 | Tons | 1100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Daikin | MPSH03C | 3 | Tons | 1100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Daikin | MPSH03C | 3 | Tons | 1100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 429395-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Daikin | MPSH05C | 5 | Tons | 2000 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
19- 719739-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YHC120E3RHA | 93.1 | MBH | 3850 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
19- 719739-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YHD180F3RHA | 149.82 | MBH | 6000 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
19- 719739-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YHD180F3RHA | 149.82 | MBH | 6000 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
19- 719739-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Trane | YHD180F3RHA | 149.82 | MBH | 6000 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
19- 719739-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Trane | RRU241E3DFA | 176.17 | MBH | 6000 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
16- 558605-2 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-C100-2 | LG | ARUN048GSS4 | 48000 | Btu/hr | 1500 | CFM | 10.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 558605-2 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-C100-3 | LG | ARUN048GSS4 | 48000 | Btu/hr | 1500 | CFM | 10.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 615057-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1-2 | Carrier | 25HCD336A006 | 24.89 | MBH | 1140 | CFM | 14 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 615057-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1-3 | Carrier | 25HCD336A006 | 24.89 | MBH | 1140 | CFM | 14 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 615057-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1-4 | Carrier | 25HCD336A006 | 16.59 | MBH | 780 | CFM | 14.5 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 615057-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2-1 | Carrier | 25HCD336A006 | 42.04 | MBH | 1720 | CFM | 13.5 | SEER | Unknown |  | Electric | Variable Volume (VAV) | N/A
16- 640577-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWA | 57.5 | MBH | 1300 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 640577-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWA | 29.8 | MBH | 950 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 640577-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWA | 35.5 | MBH | 1100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 640577-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWA | 57.5 | MBH | 1300 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 640577-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-5 | Trane | 4TWA | 29.8 | MBH | 1300 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 640577-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-6 | Trane | 4TWA | 22.3 | MBH | 900 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 662436-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Trane | YSC036G3 | 3 | Tons | 1200 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 662436-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Trane | YSC102F3 | 8.5 | Tons | 3400 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 662436-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Trane | YSC102F3 | 8.5 | Tons | 3400 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
16- 662436-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Trane | YSC102F3 | 7.5 | Tons | 3000 | CFM | 11.2 | EER |  |  | Electric | Variable Volume (VAV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP P1-1 | Carrier | 25HHA424 | 24000 | Btu/hr | 800 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-1 | Carrier | 25HBC324 | 24000 | Btu/hr | 800 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-2 | Carrier | 25HBC336 | 36000 | Btu/hr | 1200 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-3 | Carrier | 25HBC336 | 36000 | Btu/hr | 1200 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-4 | Carrier | 25HBC336 | 36000 | Btu/hr | 1600 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-6 | Carrier | 25HBC336 | 36000 | Btu/hr | 1200 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-7 | Carrier | 25HBC360 | 60000 | Btu/hr | 2000 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-8 | Carrier | 25HBC360 | 60000 | Btu/hr | 2000 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-9 | Carrier | 25HBC348 | 48000 | Btu/hr | 1600 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-10 | Carrier | 25HBC336 | 36000 | Btu/hr | 1200 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-11 | Carrier | 25HBC336 | 36000 | Btu/hr | 1200 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-12 | Carrier | 25HBC360 | 60000 | Btu/hr | 2000 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 1-13 | Carrier | 25HBC348 | 48000 | Btu/hr | 1600 | CFM | 13 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 571695-2 | VRF | Variable Refrigerant Flow | MCU-1 | Mitsubishi | PURY-P312TSLMU-A | 312000 | Btu/hr |  |  | 19.7 | IEER | 11 | EER | Electric | N/A | Yes
17- 571695-2 | VRF | Variable Refrigerant Flow | MCU-2 | Mitsubishi | PURY-P144TSLMU-A | 144000 | Btu/hr |  |  | 26.6 | IEER | 14.2 | EER | Electric | N/A | Yes
17- 571695-2 | VRF | Variable Refrigerant Flow | MCU-3 | Mitsubishi | PURY-P192TSKMU-A | 192000 | Btu/hr |  |  | 18.2 | IEER | 11.9 | EER | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-01 | Daikin | REYQ288TAYDU | 192000 | Btu/hr |  |  | 17.9 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-02 | Daikin | REYQ336TAYDU | 336000 | Btu/hr |  |  | 17.4 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-03 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 18.9 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-04 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 18.9 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-05 | Daikin | REYQ432TAYDU | 432000 | Btu/hr |  |  | 17.3 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-06 | Daikin | REYQ432TAYDU | 432000 | Btu/hr |  |  | 17.3 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-07 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 18.9 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-08 | Daikin | REYQ360TAYDU | 360000 | Btu/hr |  |  | 18.9 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-09 | Daikin | REYQ456TAYDU | 456000 | Btu/hr |  |  | 16.7 | IEER |  |  | Electric | N/A | Yes
17- 584823-1 | VRF | Variable Refrigerant Flow | VRV-4-10 | Daikin | REYQ456TAYDU | 454286 | Btu/hr |  |  | 16.7 | IEER |  |  | Electric | N/A | Yes
17- 607886-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YHC102 | 78.2 | MBH | 3935 | CFM | 12.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 607886-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YHC102 | 73.8 | MBH | 3440 | CFM | 12.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 607886-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YHC036 | 25.9 | MBH | 1090 | CFM | 12.7 | EER | 17.5 | SEER | Electric | Constant Volume (CV) | N/A
17- 607886-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Trane | YHC036 | 31.4 | MBH | 1330 | CFM | 12.7 | EER | 17.5 | SEER | Electric | Constant Volume (CV) | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-1 | Lennox | TPA042 | 3.5 | Tons |  |  | 11 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-2 | Lennox | TPA042 | 3.5 | Tons |  |  | 11 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-5 | Lennox | TPA042 | 3.5 | Tons |  |  | 11 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-6 | Lennox | TPA042 | 3.5 | Tons |  |  | 11 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-3 | Lennox | TPA036 | 3 | Tons |  |  | 11 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-4 | Lennox | TPA036 | 3 | Tons |  |  | 11 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-7 | Lennox | TPA048 | 4 | Tons |  |  | 11.5 | EER | 13 | SEER | Electric | N/A | N/A
17- 634478-1 | DHP | Ductless Heat Pump | HP-8 | Lennox | XP14018 | 1.5 | Tons |  |  | 12.5 | EER | 15.5 | SEER | Electric | N/A | N/A
17- 635582-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | TCD180B4L0OC | 12.5 | Tons | 5300 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 637259-1 | DX AHU | Direct Expansion Split System Air Handler | CRA13-18000 | Liebert | DA150DP1A | 457 | MBH | 18000 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
17- 637259-1 | DX AHU | Direct Expansion Split System Air Handler | CRA25-26000 | Liebert | VS042ADA000 | 124.2 | MBH | 6300 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-1 | Lennox | EL195UH110XE60C | 60000 | Btu/hr | 2100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-2 | Lennox | EL195UH110XE60C | 60000 | Btu/hr | 1900 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-3 | Lennox | EL195UH045XE24B | 24000 | Btu/hr | 800 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-4 | Lennox | EL195UH070XE36B | 36000 | Btu/hr | 1100 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-5 | Lennox | EL195UH070XE36B | 36000 | Btu/hr | 900 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-6 | Lennox | EL195UH070XE36B | 36000 | Btu/hr | 1200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-7 | Lennox | EL195UH110XE60C | 60000 | Btu/hr | 1950 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-8 | Lennox | EL195UH110XE60C | 60000 | Btu/hr | 2200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-9 | Lennox | EL195UH110XE60C | 60000 | Btu/hr | 2200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-10 | Lennox | EL195UH090XE48C | 48000 | Btu/hr | 1600 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 642436-1 | DX AHU | Direct Expansion Split System Air Handler | F-11 | Lennox | EL195UH070XE36B | 36000 | Btu/hr | 1175 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 653232-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Carrier | 48HC | 46.7 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-12 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-13 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-14 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-15 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-16 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-17 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-18 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-19 | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-20A | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-20B | Carrier | CARRIER 48TC-A06 STANDARD EFFICIENCY | 54.9 | MBH | 2000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-21A | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-21B | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-24A | Carrier | CARRIER 48TC-TE24 STANDARD EFFICIENCY | 229.1 | MBH | 8000 | CFM | 9.8 | EER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-24B | Carrier | CARRIER 48TC-TE24 STANDARD EFFICIENCY | 229.1 | MBH | 8000 | CFM | 9.8 | EER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-25 | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1200 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-26 | Carrier | CARRIER 48ES-A30 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13.5 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-27 | Carrier | CARRIER 48ES-A30 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13.5 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-28 | Carrier | CARRIER 48TC-A05 STANDARD EFFICIENCY | 39.4 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29A | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29B | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29C | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29D | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29E | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29F | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29G | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-29H | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
16- 505459-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-30 | Carrier | CARRIER 48TC-A04 STANDARD EFFICIENCY | 30.1 | MBH | 1000 | CFM | 13 | SEER |  |  | Electric | 2-Speed | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- A1 | Daikin | MPS025B | 273.9 | MBH | 9000 | CFM | 10 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- A2 | Daikin | MPSA03C | 31.6 | MBH | 1200 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- A3 | Daikin | MPS025B | 273.9 | MBH | 9000 | CFM | 10 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- B1 | Daikin | DCG150 | 138.1 | MBH | 5000 | CFM | 10.8 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- B2 | Daikin | DCG150 | 138.1 | MBH | 5000 | CFM | 10.8 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- B3 | Daikin | MPSA04C | 42.2 | MBH | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- C1 | Daikin | DCG102 | 83.6 | MBH | 3000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- C2 | Daikin | MPSA03C | 32 | MBH | 1200 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- C4 | Daikin | MPSA04C | 44.6 | MBH | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- C3 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- C5 | Daikin | DCG102 | 83.6 | MBH | 3000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- D1 | Daikin | DCG090 | 76.1 | MBH | 2800 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- D2 | Daikin | MPSA05c | 55.9 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- D3 | Daikin | MPSA05c | 55.9 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- D4 | Daikin | MPSA05c | 55.9 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- E1 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- E2 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- E3 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- E4 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- F1 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- F2 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- F3 | Daikin | DCG120 | 105.9 | MBH | 4000 | CFM | 11.3 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- E5 | Daikin | MPSA05C | 55.9 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 672586-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU- F4 | Daikin | MPSA05C | 55.9 | MBH | 2000 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 674429-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU‐1 | TRANE | YSC102F3 | 90.87 | MBH | 3980 | CFM | 11.2 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
17- 674429-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU‐2 | TRANE | YSC102F3 | 91.18 | MBH | 3900 | CFM | 11.2 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
17- 674429-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU‐3 | TRANE | YSC102F3 | 66.68 | MBH | 2600 | CFM | 11.2 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
17- 674429-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU‐4 | TRANE | YSD150F3 | 109.34 | MBH | 4200 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 674429-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU‐5 | TRANE | YSC036G3 | 33.4 | MBH | 1400 | CFM | 11.2 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
17- 676005-1 | DX AHU | Direct Expansion Split System Air Handler | CU-1 | Carrier | 59SP5-060-14 | 42.6 | MBH | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 676005-1 | DX AHU | Direct Expansion Split System Air Handler | CU-2 | Carrier | 59SP5-060-14 | 42.6 | MBH | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 676005-1 | DX AHU | Direct Expansion Split System Air Handler | CU-3 | Carrier | 59SP5-060-14 | 42.6 | MBH | 1600 | CFM | 14 | SEER |  |  | Electric | Constant Volume (CV) | N/A
16- 507255-1 [Corridors] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48HC-D08 | 89 | MBH | 1950 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 697310-1 | VRF | Variable Refrigerant Flow | OCU-1 | Mitsubishi | PURY-P168TLMU-A | 165 | MBH |  |  | 19.6 | IEER | Unknown |  | Electric | N/A | Yes
17- 716517-1 | DHP | Ductless Heat Pump | CU-1 | Mitsubishi | PUY-A36NHA4 | 35000 | Btu/hr |  |  | 14.2 | SEER |  |  | Electric | N/A | N/A
17- 716517-1 | DHP | Ductless Heat Pump | CU-2 | Mitsubishi | PUY-A36NHA4 | 35000 | Btu/hr |  |  | 14.2 | SEER |  |  | Electric | N/A | N/A
17- 719811-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 1 | AAON | RN | 346.5 | MBH | 1200 | CFM | 12.6 | IEER |  |  | Electric | Variable Volume (VAV) | N/A
17- 719811-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 2 | AAON | RN | 141.6 | MBH | 4560 | CFM | 15.4 | IEER |  |  | Electric | Variable Volume (VAV) | N/A
17- 719811-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU 3 | AAON | RN | 140.7 | MBH | 4470 | CFM | 15.4 | IEER |  |  | Electric | Variable Volume (VAV) | N/A
17- 521675-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP 6-1 | Carrier | 25HBC324 | 24000 | Btu/hr | 800 | CFM | Unknown |  |  |  | Electric | Constant Volume (CV) | N/A
17- 594224-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Bard | W36HA | 34600 | Btu/hr | 1100 | CFM | 10 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWR5036H1 | 36 | MBH | 1070 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWR5048H1 | 48 | MBH | 1650 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 777891-1 [Common area] | VRF | Variable Refrigerant Flow | AMOU-1 | Mitsubishi | PURY-P240YSLMU-A | 240 | MBH |  |  | 12.9 | EER | 22.3 | IEER | Electric | N/A | No
17- 777891-1 [Common area] | VRF | Variable Refrigerant Flow | AMOU-2 | Mitsubishi | PURY-P336YSLMU-A | 336 | MBH |  |  | 9.9 | EER | 15.3 | IEER | Electric | N/A | No
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-1.1 | LG | ARUM504DTE5 | 42 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-1.2 | LG | ARUM504DTE5 | 42 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-2.1 | LG | ARUM504DTE5 | 42 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-2.2 | LG | ARUM504DTE5 | 42 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-3.1 | LG | ARUM504DTE5 | 42 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-3.2 | LG | ARUM504DTE5 | 42 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-4.1 | LG | ARUM384DTE5 | 32 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-4.2 | LG | ARUM384DTE5 | 32 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-4.3 | LG | ARUM384DTE5 | 32 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-5.1 | LG | ARUM384DTE5 | 32 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-5.2 | LG | ARUM384DTE5 | 32 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 778018-1 | VRF | Variable Refrigerant Flow | RCU-5.3 | LG | ARUM384DTE5 | 32 | Tons |  |  | 12.5 | EER |  |  | Electric | N/A | Unknown
17- 792314-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RRU-2 | Trane | RRU240F3DFA | 224 | MBH | 5000 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 792314-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YHC092 | 84 | MBH | 3200 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 792314-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YHC092 | 85 | MBH | 3300 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 792314-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YHC072 | 54 | MBH | 2500 | CFM | 12.6 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 792314-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RRU-1 | Trane | RRU120E3DUA | 120 | MBH | 3800 | CFM | 14 | IEER |  |  | Electric | Constant Volume (CV) | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-2 | Mitsubishi | PUZ-A36NKA7 | 36 | MBH |  |  | 21.8 | SEER |  |  | Electric | N/A | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-3 | Mitsubishi | MUZ-GL12NA | 12 | MBH |  |  | 23.1 | SEER |  |  | Electric | N/A | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-4 | Mitsubishi | MUZ-GL24NA | 21.5 | MBH |  |  | 20.5 | SEER |  |  | Electric | N/A | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-5 | Mitsubishi | PUZ-A42NKA7 | 42 | MBH |  |  | 21 | SEER |  |  | Electric | N/A | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-6 | Mitsubishi | PUZ-A42NKA7 | 42 | MBH |  |  | 21 | SEER |  |  | Electric | N/A | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-7 | Mitsubishi | PUZ-A36NKA7 | 36 | MBH |  |  | 21.8 | SEER |  |  | Electric | N/A | N/A
17- 803573-1 [Misc.] | DHP | Ductless Heat Pump | OHP-8 | Mitsubishi | PUZ-A30NKA7 | 30 | MBH |  |  | 22.8 | SEER |  |  | Electric | N/A | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWR5024H1 | 24 | MBH | 765 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWR5048H1 | 48 | MBH | 1745 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-5 | Trane | 4TWR5024H1 | 24 | MBH | 700 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-6 | Trane | 4TWR5030H1 | 30 | MBH | 1000 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-7 | Trane | 4TWR5048H1 | 48 | MBH | 1700 | CFM | 12.5 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Daikin | RPS045D | 530 | MBH | 15650 | CFM | 10.5 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Daikin | DPS016A | 177 | MBH | 4800 | CFM | 20.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Daikin | DPS020A | 252 | MBH | 7800 | CFM | 20.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Daikin | RPS063D | 627 | MBH | 16480 | CFM | 10 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Daikin | RPS051D | 578 | MBH | 23635 | CFM | 10.2 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Daikin | RPS045D | 514 | MBH | 17940 | CFM | 10.5 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Daikin | RPS071D | 825 | MBH | 29560 | CFM | 9.7 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Daikin | RPS110D | 1185 | MBH | 42090 | CFM | 10.5 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Daikin | RPS051D | 612 | MBH | 22395 | CFM | 10.2 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Daikin | RPS045D | 502 | MBH | 22200 | CFM | 10.5 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Daikin | DPS016A | 172 | MBH | 6880 | CFM | 20.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-12 | Daikin | DPS020A | 264 | MBH | 7480 | CFM | 20.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-13 | Daikin | MPS030F | 338 | MBH | 12800 | CFM | 10.3 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-14 | Daikin | MPS040F | 458 | MBH | 12260 | CFM | 10.2 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-15 | Daikin | DPS016A | 187 | MBH | 6500 | CFM | 20.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 735523-1 [Classrooms, commons, misc.] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-16 | Daikin | RPS071D | 773 | MBH | 22400 | CFM | 9.7 | EER |  |  | Electric | Variable Volume (VAV) | N/A
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-1A | Daikin | REYQ96TTJU | 79.1 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-1B | Daikin | REYQ96TTJU | 78.4 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-1C | Daikin | REYQ96TTJU | 77 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-1D | Daikin | REYQ96TTJU | 79.2 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-1E | Daikin | REYQ216TTJU | 185.1 | MBH |  |  | 12 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-2A | Daikin | REYQ96TTJU | 79.4 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-2B | Daikin | REYQ96TTJU | 79 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-2C | Daikin | REYQ120TTJU | 98.4 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-2D | Daikin | REYQ96TTJU | 80.4 | MBH |  |  | 13 | EER |  |  | Electric | N/A | No
17- 813087-1 | VRF | Variable Refrigerant Flow | HRU-2E | Daikin | REYQ192TTJU | 163.7 | MBH |  |  | 12 | EER |  |  | Electric | N/A | No
17- 815466-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Lennox | LGH092H4MM3Y | 7.5 | Tons | 3250 | CFM | Unknown |  |  |  | Electric | Variable Volume (VAV) | N/A
17- 815466-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Lennox | LGH300H4MH3Y | 25 | Tons | 10500 | CFM | Unknown |  |  |  | Electric | Variable Volume (VAV) | N/A
17- 821806-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | FUR-1 | Carrier | 59MN5A060V17-14 | 3 | Tons | 1335 | CFM | 15.5 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
17- 821806-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | FUR-2 | Carrier | 59MN5A060V17-20 | 4 | Tons | 1945 | CFM | 15 | SEER |  |  | Electric | Variable Volume (VAV) | N/A
17- 830379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-1 | Unknown | Unknown | 48 | MBH | Unknown |  | 17.6 | SEER |  |  | Electric | Unknown | N/A
17- 830379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-3 | Unknown | Unknown | 36 | MBH | Unknown |  | 18 | SEER |  |  | Electric | Unknown | N/A
17- 830379-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RT-2 | Unknown | Unknown | 72 | MBH | Unknown |  | 12 | SEER |  |  | Electric | Unknown | N/A
17- 832860-1 [Living area] | VRF | Variable Refrigerant Flow | VRF System A | Daikin | RQEYQ168PCTJ-HR | 160 | MBH |  |  | 23.1 | EER |  |  | Electric | N/A | Yes
17- 855496-1 [Living] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | AAON | RN011 | 107 | MBH | 4000 | CFM | 13.1 | EER | 18.8 | IEER | Electric | Variable Volume (VAV) | N/A
17- 855496-1 [Living] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | AAON | RQ002 | 21 | MBH | 800 | CFM | 14.75 | EER | 19.15 | IEER | Electric | Variable Volume (VAV) | N/A
17- 856087-1 | VRF | Variable Refrigerant Flow | HP-1 | Mitsubishi | PUHY-P96TLMU-A | 99.5 | MBH | 370 | CFM | 28.2 | IEER |  |  | Electric | N/A | No
17- 866279-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YSC06CE4-e | 89000 | Btu/hr | 2000 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 866279-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YSC036CE4-e | 36000 | Btu/hr | 1220 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 866279-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YSC036CE4-e | 36000 | Btu/hr | 1220 | CFM | 11.2 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 686039-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | South-2 | Lennox | ZGA120S4BS1Y | 10 | Tons |  |  | 12 | SEER | 11 | EER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Trane | 4WCY5024A1000A | 25 | MBH | 700 | CFM | 12 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
18- 560625-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48LC-14 | 149.9 | MBH | 5000 | CFM | 12.4 | EER |  |  | Electric | Variable Volume (VAV) | N/A
18- 560625-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48LC-12 | 122.1 | MBH | 4250 | CFM | 13 | EER |  |  | Electric | Variable Volume (VAV) | N/A
17- 636076-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Trane | WSC120 | 124 | MBH | 4100 | CFM | 11.2 | EER | 13.1 | SEER | Electric | 2-Speed | N/A
17- 636076-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Trane | 4WCY5024A1000A | 25 | MBH | 710 | CFM | 12 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Trane | WSC072 | 72 | MBH | 2625 | CFM | 11.4 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
17- 636076-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-5 | Trane | WSC090 | 93 | MBH | 3150 | CFM | 11.1 | EER | 12.2 | SEER | Electric | Constant Volume (CV) | N/A
18- 576787-1 | DHP | Ductless Heat Pump | CU-1 | Mitsubishi | PUMY-P36NKMU1 | 36 | MBH |  |  | 15.6 | SEER |  |  | Electric | N/A | N/A
18- 576787-1 | DHP | Ductless Heat Pump | CU-2 | Mitsubishi | PUMY-P60NKMU1 | 60 | MBH |  |  | 17 | SEER |  |  | Electric | N/A | N/A
18- 576787-1 | DHP | Ductless Heat Pump | CU-3 | Mitsubishi | PUMY-P60NKMU1 | 60 | MBH |  |  | 17 | SEER |  |  | Electric | N/A | N/A
18- 585712-1 | VRF | Variable Refrigerant Flow | HP-1 | LG | ARWB336DAS4 | 289700 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
18- 585712-1 | VRF | Variable Refrigerant Flow | HP-2 | LG | ARWB192DAS4 | 153400 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
18- 585712-1 | VRF | Variable Refrigerant Flow | HP-3 | LG | ARWB288DAS4 | 230100 | Btu/hr |  |  | Unknown |  |  |  | Electric | N/A | Yes
17- 803573-1 [Pad] | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | York | XP180C00R2A1AAA1A1 | 15 | Tons | 6000 | CFM | 10.6 | SEER |  |  | Electric | Constant Volume (CV) | N/A
17- 808067-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Carrier | 50KCQA04 | 23.31 | MBH | 895 | CFM | 14 | SEER | 12.1 | EER | Electric | Constant Volume (CV) | N/A
17- 808067-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Carrier | 50TCQD08 | 87.61 | MBH | 3210 | CFM | 12.5 | IEER | 11.2 | EER | Electric | Constant Volume (CV) | N/A
17- 808067-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Carrier | 50KCQA05 | 43.58 | MBH | 1590 | CFM | 14.3 | SEER | 12 | EER | Electric | Constant Volume (CV) | N/A
18- 625157-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YSC09H3RMA | 73.8 | MBH | 3000 | CFM | 11.2 | EER | 13.4 | SEER | Electric | Constant Volume (CV) | N/A
18- 641081-1 | DX AHU | Direct Expansion Split System Air Handler | CDBC-HTP-01 | Trane | WSC060 | 64.98 | MBH | 2000 | CFM | Unknown |  |  |  | Electric | Variable Volume (VAV) | N/A
18- 641081-1 | DX AHU | Direct Expansion Split System Air Handler | CDBC-HTP-02 | Trane | WSC060 | 64.98 | MBH | 2000 | CFM | Unknown |  |  |  | Electric | Variable Volume (VAV) | N/A
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R11 | LG | Arum | 24 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R12 | LG | Arum | 8 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R21 | LG | Arum | 28 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R22 | LG | Arum | 22 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R31 | LG | Arum | 18 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R32 | LG | Arum | 18 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R41 | LG | Arum | 18 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R42 | LG | Arum | 18 | Tons |  |  | 15.2 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R51 | LG | Arum | 16 | Tons |  |  | 14.1 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R52 | LG | Arum | 18 | Tons |  |  | 14.1 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R61 | LG | Arum | 28 | Tons |  |  | 14.1 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R62 | LG | Arum | 24 | Tons |  |  | 14.1 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R63 | LG | Arun | 18 | Tons |  |  | 14.1 | EER |  |  | Electric | N/A | Yes
18- 650512-1 | VRF | Variable Refrigerant Flow | OU-R64 | LG | Arun | 2 | Tons |  |  | 15.8 | EER |  |  | Electric | N/A | Yes
18- 596289-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Lennox | LGH156H4M | 118632 | Btu/hr | 5100 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 596289-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Lennox | LGH156H4M | 118632 | Btu/hr | 5100 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 596289-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Lennox | LGH156H4M | 118632 | Btu/hr | 5100 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 596289-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Lennox | LGH156H4M | 118632 | Btu/hr | 5100 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 596289-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Lennox | LGH092H4M | 71627 | Btu/hr | 3200 | CFM | 12.5 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-1-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-2-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-3-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-4-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-5-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-6-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-7-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-8-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-9-1 | Mitsubishi | PURY-336YLMU-A | 336000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-1-2 | Mitsubishi | PURY-216YLMU-A | 216000 | Btu/hr |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-2-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-3-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-4-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-5-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-6-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-7-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-8-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 704117-1 | VRF | Variable Refrigerant Flow | HP-9-2 | Mitsubishi | PURY-168YLMU-A | 168000 | Btu/hr |  |  | 11.2 | EER |  |  | Electric | N/A | Yes
18- 718226-1 [AHU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Daikin | RPS045D | 512 | MBH | 18125 | CFM | 10.5 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
18- 718226-1 [AHU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Daikin | RPS045D | 484 | MBH | 16350 | CFM | 10.4 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
18- 718226-1 [AHU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Daikin | RPS035D | 361 | MBH | 13150 | CFM | 10.2 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
18- 718226-1 [AHU] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Daikin | RPS021D | 250 | MBH | 9475 | CFM | 10.3 | EER | N/A |  | Electric | Variable Volume (VAV) | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-1 | Mitsubishi | PUZ-A36 | 34.2 | MBH |  |  | 14 | SEER | N/A |  | Electric | N/A | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-6 | Mitsubishi | PUZ-A36 | 34.2 | MBH |  |  | 14 | SEER | N/A |  | Electric | N/A | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-2 | Mitsubishi | PUZ-A33 | 30 | MBH |  |  | 15.5 | SEER | N/A |  | Electric | N/A | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-5 | Mitsubishi | PUZ-A33 | 30 | MBH |  |  | 15.5 | SEER | N/A |  | Electric | N/A | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-7 | Mitsubishi | PUZ-A33 | 30 | MBH |  |  | 15.5 | SEER | N/A |  | Electric | N/A | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-3 | Mitsubishi | PUZ-A24 | 24 | MBH |  |  | 17 | SEER | N/A |  | Electric | N/A | N/A
18- 718226-1 [DHP] | DHP | Ductless Heat Pump | CU-4 | Mitsubishi | PUZ-A42 | 42 | MBH |  |  | 21 | SEER | N/A |  | Electric | N/A | N/A
17- 808067-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Carrier | 50TCQA07 | 57.96 | MBH | 1940 | CFM | 12.5 | IEER | 11.1 | EER | Electric | Constant Volume (CV) | N/A
18- 542998-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | AAON | RN-009-2-0-E60E-569 | 85000 | Btu/hr | 2200 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 571936-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-1 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 15.5 | SEER |  |  | Electric | Unknown | N/A
18- 571936-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-2 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 15.5 | SEER |  |  | Electric | Unknown | N/A
18- 571936-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-3 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 15.5 | SEER |  |  | Electric | Unknown | N/A
18- 571936-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-4 | Payne | PH15NB018 | 18 | MBH | 600 | CFM | 15.5 | SEER |  |  | Electric | Unknown | N/A
18- 612115-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Daikin | DZ | 17400 | Btu/hr | 600 | CFM | 14 | SEER | 11.5 | EER | Electric | Constant Volume (CV) | N/A
18- 612115-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | Daikin | DZ | 23200 | Btu/hr | 840 | CFM | 14 | SEER | 11.5 | EER | Electric | Constant Volume (CV) | N/A
18- 612115-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Daikin | DZ | 60000 | Btu/hr | 1800 | CFM | 14 | SEER | 11.5 | EER | Electric | Constant Volume (CV) | N/A
18- 723839-1 | VRF | Variable Refrigerant Flow | HP-1 | LG | ARUM168BTE5 | 168000 | Btu/hr |  |  | 12.3 | IEER | 10.6 | EER | Electric | N/A | No
18- 723839-1 | VRF | Variable Refrigerant Flow | HP-2 | LG | ARUM241BTE5 | 240000 | Btu/hr |  |  | 12.3 | IEER | 10.6 | EER | Electric | N/A | No
18- 612115-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | Daikin | DZ | 36000 | Btu/hr | 262 | CFM | 17.7 | SEER | 9.2 | EER | Electric | Constant Volume (CV) | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-1 | Trane | 4TTR6024 | 21088 | Btu/hr | 850 | CFM | 13.5 | EER |  |  | Electric | Unknown | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-2 | Trane | 4TTR6018 | 16626 | Btu/hr | 615 | CFM | 14.5 | EER |  |  | Electric | Unknown | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-3 | Trane | 4TTR6024 | 20434 | Btu/hr | 840 | CFM | 13.5 | EER |  |  | Electric | Unknown | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-4 | Trane | 4TTR6048 | 41740 | Btu/hr | 1660 | CFM | 13 | EER |  |  | Electric | Unknown | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-5 | Trane | 4TTR6048 | 42450 | Btu/hr | 1720 | CFM | 13 | EER |  |  | Electric | Unknown | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-6 | Trane | 4TTR6030 | 26475 | Btu/hr | 1150 | CFM | 14 | EER |  |  | Electric | Unknown | N/A
18- 785631-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | 36-RTU-01 | Carrier | 48LCE20 | 178.5 | MBH | 7000 | CFM | 11.2 | EER | 16.6 | IEER | Electric | Variable Volume (VAV) | N/A
18- 785631-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | 36-RTU-02 | Carrier | 48LCE20 | 178.5 | MBH | 7000 | CFM | 11.2 | EER | 16.6 | IEER | Electric | Variable Volume (VAV) | N/A
18- 785631-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | 36-RTU-03 | Carrier | 48LCE20 | 178.5 | MBH | 7000 | CFM | 11.2 | EER | 16.6 | IEER | Electric | Variable Volume (VAV) | N/A
18- 625974-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | CU-7 | Trane | 4TTR6042 | 37697 | Btu/hr | 1450 | CFM | 13.5 | EER |  |  | Electric | Unknown | N/A
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-01 | Mitsubishi | Unknown | 18 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-03 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-04 | Mitsubishi | Unknown | 12 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-05 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-06 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-07 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-08 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-09 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-10 | Mitsubishi | Unknown | 6 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-11 | Mitsubishi | Unknown | 8 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-02 | Mitsubishi | Unknown | 15 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-12 | Mitsubishi | Unknown | 8 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 863748-1 | VRF | Variable Refrigerant Flow | VRF-13 | Mitsubishi | Unknown | 8 | MBH |  |  | Unknown |  |  |  | Electric | N/A | No
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-0.1 | Carrier | 48HC-017 High Efficiency | 168.5 | MBH | 6000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-0.2 | Carrier | 48HC-009 High Efficiency | 95.6 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1.1 | Carrier | 48HC-009 High Efficiency | 95.6 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1.2 | Carrier | 48HC-005 High Efficiency | 46.3 | MBH | 1600 | CFM | 15.6 | SEER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2.1 | Carrier | 48HC-004 High Efficiency | 46.3 | MBH | 1200 | CFM | 15 | SEER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2.2 | Carrier | 48HC-008 High Efficiency | 86.1 | MBH | 3000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3.1 | Carrier | 48HC-008 High Efficiency | 86.1 | MBH | 3000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3.4 | Carrier | 48HC-008 High Efficiency | 86.1 | MBH | 3000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3.2 | Carrier | 48HC-017 High Efficiency | 168.5 | MBH | 6000 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3.3 | Carrier | 48HC-006 High Efficiency | 56.3 | MBH | 2000 | CFM | 15.2 | SEER |  |  | Electric | Constant Volume (CV) | N/A
18- 899620-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3.5 | Carrier | 48HC-007 High Efficiency | 68.7 | MBH | 2400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 672421-1 | DHP | Ductless Heat Pump | HP-1B | Mitsubishi | PUZ-A18NKA7 | 18 | MBH |  |  | 11.4 | EER |  |  | Electric | N/A | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YSC072 | 65.33 | MBH | 2250 | CFM | 11.2 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YSC072 | 65.33 | MBH | 2250 | CFM | 11.2 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YSC072 | 65.33 | MBH | 2250 | CFM | 11.2 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Trane | YSC048 | 44.59 | MBH | 1800 | CFM | 13.4 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Trane | YSD150 | 130.43 | MBH | 4500 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Trane | YSD150 | 130.43 | MBH | 4500 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Trane | YSD150 | 130.43 | MBH | 4500 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Trane | YSD150 | 130.43 | MBH | 4500 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Trane | YSC072 | 67.99 | MBH | 2250 | CFM | 11.2 | EER | 13 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Trane | YSD150 | 130.43 | MBH | 4500 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Trane | YSD210 | 188.46 | MBH | 7875 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-12 | Trane | YSH180 | 165.78 | MBH | 6750 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-13 | Trane | YSD150 | 130.43 | MBH | 4500 | CFM | 11 | EER |  |  | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-14 | Trane | YSC036 | 36.19 | MBH | 1350 | CFM | 12.7 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-15 | Trane | YSC036 | 36.19 | MBH | 1350 | CFM | 12.7 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
19- 700419-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-16 | Trane | YSC036 | 36.19 | MBH | 1350 | CFM | 12.7 | EER | 15 | SEER | Electric | Constant Volume (CV) | N/A
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-1 | LG | ARUM241DTE5 | 234 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-3 | LG | ARUM241DTE5 | 234 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-1.1 | LG | ARUM384DTE5 | 384 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-1.2 | LG | ARUM384DTE5 | 384 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-2.1 | LG | ARUM312DTE5 | 312 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-2.2 | LG | ARUM336DTE5 | 336 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-2.3 | LG | ARUM312DTE5 | 312 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-3.1 | LG | ARUM312DTE5 | 312 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-3.2 | LG | ARUM336DTE5 | 336 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-3.3 | LG | ARUM312DTE5 | 312 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-4.1 | LG | ARUM312DTE5 | 312 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-4.2 | LG | ARUM336DTE5 | 336 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-4.3 | LG | ARUM312DTE5 | 312 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Yes
19- 730078-1 | VRF | Variable Refrigerant Flow | RCU-4.3 | LG | ARUM312DTE5 | 351 | MBH |  |  | Unknown |  | Unknown |  | Electric | N/A | Unknown
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 10.3 | EER | 18 | SEER | Electric | Unknown | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 10.3 | EER | 18 | SEER | Electric | Unknown | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 9.8 | EER | 18 | SEER | Electric | Unknown | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 9.8 | EER | 18 | SEER | Electric | Unknown | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#1 | Lennox | KGA120H4BM-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#2 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#3 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#4 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#5 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#6 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#7 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#8 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#9 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#10 | Lennox | KGA120H4BS-G | 124800 | Btu/hr | 4000 | CFM | 12 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#11 | Lennox | KGB048S4DM-G | 49700 | Btu/hr | 1600 | CFM | 11.5 | EER | 14 | IEER | Electric | Constant Volume (CV) | N/A
18- 596300-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | HL#12 | Lennox | KGB048S4DM-G | 86000 | Btu/hr | 1600 | CFM | 11.5 | EER | 14 | IEER | Electric | Constant Volume (CV) | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-5 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 9.8 | EER | 18 | SEER | Electric | Unknown | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-6 | Daikin | RXTQ60TAVJU | 5 | Tons |  |  | 9.8 | EER | 18 | SEER | Electric | Unknown | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-7 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 10.3 | EER | 18 | SEER | Electric | Unknown | N/A
19- 937126-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#1 | Lennox | LGH300H4M | 319.9 | MBH | 10000 | CFM | 11.6 | EER | 14.4 | IEER | Electric | Constant Volume (CV) | N/A
19- 937126-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#2 | Lennox | LGH094U4M | 95.1 | MBH | 3000 | CFM | 13.4 | EER | 20.7 | IEER | Electric | Constant Volume (CV) | N/A
19- 937126-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#3 | Lennox | LGH300H4M | 307.9 | MBH | 8000 | CFM | 11.6 | EER | 14.4 | IEER | Electric | Constant Volume (CV) | N/A
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-4W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-6W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3/4W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2/3W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5/6W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-4SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-6SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2/3SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3/4SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5/6SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-4N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-6N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2/3N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3/4N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5/6N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-1S | Mitsubishi | PURY-P288YSKMU-A | 24 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-1N | Mitsubishi | PURY-P288YSKMU-A | 24 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-1N | Mitsubishi | PURY-P288YSKMU-A | 24 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-1S | Mitsubishi | PURY-P288YSKMU-A | 24 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2/3N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2/3SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2/3W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-2W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3/4N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3/4SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3/4W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-3W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-4N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-4SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-4W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5/6N | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5/6SE | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5/6W | Mitsubishi | PURY-P72YKMU-A | 6 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-5W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-6N | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-6SE | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Unknown
98- 927699-1 | VRF | Variable Refrigerant Flow | HP-6W | Mitsubishi | PURY-P96YKMU-A | 8 | Tons |  |  | Unknown |  |  |  | Electric | N/A | Yes
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-8 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 10.3 | EER | 18 | SEER | Electric | Unknown | N/A
15- 689971-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YSC | 43.5 | MBH | 1990 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
15- 689971-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YSC | 31.7 | MBH | 1400 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
15- 689971-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YSC | 37.3 | MBH | 1600 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
15- 689971-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Trane | YSC | 49.1 | MBH | 1990 | CFM | 13 | SEER |  |  | Electric | Unknown | N/A
15- 689971-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Trane | YSC | 54.4 | MBH | 2800 | CFM | 11 | EER |  |  | Electric | Unknown | N/A
15- 689971-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Trane | YSC | 37.4 | MBH | 3000 | CFM | 11 | EER |  |  | Electric | Unknown | N/A
18- 718902-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-9 | Daikin | RXTQ48TAVJU | 4 | Tons |  |  | 10.3 | EER | 18 | SEER | Electric | Unknown | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | York | THE418B31S | 41.6 | MBH | 1500 | CFM | 14.25 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | York | YHE24B21S | 21.3 | MBH | 750 | CFM | 14 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | York | THE60B31S | 46.9 | MBH | 1900 | CFM | 14.25 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
14- 579875-1 | DHP | Ductless Heat Pump | CU-1 | Carrier | 25HCE448A003 | 4 | Tons |  |  | 11.7 | EER | 14 | SEER | Electric | N/A | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | York | THE60B31S | 48.6 | MBH | 1900 | CFM | 14.25 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-5 | York | THE30B31S | 25.3 | MBH | 900 | CFM | 14 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-6 | York | THE36B31S | 28.8 | MBH | 1100 | CFM | 15.25 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 737861-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-7 | York | THE48B31S | 39.5 | MBH | 1550 | CFM | 15 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 811956-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Lennox | 14HPX-024-230 | 25200 | Btu/hr | 900 | CFM | 16 | SEER |  |  | Electric | Constant Volume (CV) | N/A
18- 908206-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | HP-1 | Carrier | 50HCQD08 | 84.9 | MBH | 3000 | CFM | 12.1 | EER | 12.8 | IEER | Electric | Constant Volume (CV) | N/A
19- 506267-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWA4036A3 | 31.7 | MBH | 1190 | CFM | 14.75 | SEER |  |  | Electric | Constant Volume (CV) | N/A
19- 506267-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWA4060A3 | 53.6 | MBH | 1840 | CFM | 14.5 | SEER |  |  | Electric | Constant Volume (CV) | N/A
19- 506267-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWA4060A3 | 53.6 | MBH | 1840 | CFM | 14.5 | SEER |  |  | Electric | Constant Volume (CV) | N/A
19- 506267-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWA4060A3 | 53.6 | MBH | 1840 | CFM | 14.5 | SEER |  |  | Electric | Constant Volume (CV) | N/A
19- 731945-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-1 | Carrier | 50KCQA06 | 49.1 | MBH | 2000 | CFM | 14 | SEER | 12.2 | EER | Electric | Variable Volume (VAV) | N/A
16- 709134-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | SF-090 | 908 | MBH | 74500 | CFM | 10.4 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 709134-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | SF-090 | 908 | MBH | 74500 | CFM | 10.4 | EER |  |  | Electric | Variable Volume (VAV) | N/A
16- 709134-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YHD300 | 274 | MBH | 20000 | CFM | 10.6 | EER |  |  | Electric | Variable Volume (VAV) | N/A
18- 554364-1 [Administrative] | VRF | Variable Refrigerant Flow | HP-1 | Mitsubishi | PURY-P336YSLMU-A | 394.4 | MBH |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 554364-1 [Administrative] | VRF | Variable Refrigerant Flow | HP-2 | Mitsubishi | PURY-P336YSLMU-A | 339.2 | MBH |  |  | 9.7 | EER |  |  | Electric | N/A | Yes
18- 554364-1 [Kitchen & Whitebox] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48A2-027 High Efficiency | 274 | MBH | 10000 | CFM | 10 | EER |  |  | Electric | Variable Volume (VAV) | N/A
18- 554364-1 [Kitchen & Whitebox] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48HC-D08 High Efficiency | 86.1 | MBH | 3000 | CFM | 12 | EER |  |  | Electric | Variable Volume (VAV) | N/A
11- 556107-1 | VRF | Variable Refrigerant Flow | CU 5-1 | LG | ARUM360DTE5 | 360 | MBH |  |  | 10.2 | EER | 19.5 | IEER | Electric | N/A | No
11- 556107-1 | VRF | Variable Refrigerant Flow | CU 5-2 | LG | ARUM408DTE5 | 408 | MBH |  |  | 9.7 | EER | 19 | IEER | Electric | N/A | No
11- 556107-1 | VRF | Variable Refrigerant Flow | CU 5-3 | LG | ARUM480DTE5 | 480 | MBH |  |  | 9.7 | EER | 18 | IEER | Electric | N/A | No
11- 556107-1 | VRF | Variable Refrigerant Flow | CU 5-4 | LG | ARUN024GSS4 | 24 | MBH |  |  | 9.7 | EER | 18 | IEER | Electric | N/A | No
16- 442030-1 | DHP | Ductless Heat Pump | CU-1-1 | LG | ARUN060GSS4 | 60 | MBH |  |  | 16.5 | SEER | N/A |  | Electric | N/A | N/A
16- 442030-1 | DHP | Ductless Heat Pump | CU-7-2 | LG | ARUN024GSS4 | 24.2 | MBH |  |  | 15.8 | SEER | N/A |  | Electric | N/A | N/A
16- 442030-1 | DHP | Ductless Heat Pump | CU-7-3 | LG | ARUN048GSS4 | 48.5 | MBH |  |  | 17 | SEER | N/A |  | Electric | N/A | N/A
16- 442030-1 | DHP | Ductless Heat Pump | CU-1-2 | LG | LSN360HV | 34 | MBH |  |  | 16.1 | SEER | N/A |  | Electric | N/A | N/A
16- 442030-1 | DHP | Ductless Heat Pump | CU-R-1 | LG | LSU360HV | 34 | MBH |  |  | 16.1 | SEER | N/A |  | Electric | N/A | N/A
16- 442030-1 | DHP | Ductless Heat Pump | CU-R-2 | LG | ARUN038GSS4 | 34.5 | MBH |  |  | 17 | SEER | N/A |  | Electric | N/A | N/A
16- 442030-1 | DHP | Ductless Heat Pump | CU-R-3 | LG | ARUN038GSS4 | 25 | MBH |  |  | 17 | SEER | N/A |  | Electric | N/A | N/A
16- 615127-1 | VRF | Variable Refrigerant Flow | CU-1 | LG | ARUB384DTE4 | 331.9 | MBH |  |  | 23.1 | IEER |  |  | Electric | N/A | Yes
16- 615127-1 | VRF | Variable Refrigerant Flow | CU-2 | LG | ARUB337DTE4 | 261.4 | MBH |  |  | 19.6 | IEER |  |  | Electric | N/A | Yes
19- 731945-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-2 | Carrier | 50HCQD07 | 62.7 | MBH | 2000 | CFM | 15.8 | SEER | 12.1 | EER | Electric | Variable Volume (VAV) | N/A
19- 731945-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-3 | Carrier | 50TCQD12 | 98.6 | MBH | 4000 | CFM | 13.4 | SEER | 11.2 | EER | Electric | Variable Volume (VAV) | N/A
19- 731945-1 | ASHP RTU | Air Source Heat Pump (Packaged Rooftop) | RTU-4 | Carrier | 50KCQA06 | 49.7 | MBH | 2000 | CFM | 14 | SEER | 12.2 | EER | Electric | Variable Volume (VAV) | N/A
19- 765123-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-1 | Trane | 4TWV8036A | 42000 | Btu/hr | 1400 | CFM | 12.5 | EER | 18 | SEER | Electric | Variable Volume (VAV) | N/A
19- 765123-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-2 | Trane | 4TWR4030G | 36000 | Btu/hr | 1200 | CFM | 12 | EER | 14.5 | SEER | Electric | Variable Volume (VAV) | N/A
19- 765123-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWV8036A | 42000 | Btu/hr | 1400 | CFM | 12.5 | EER | 18 | SEER | Electric | Variable Volume (VAV) | N/A
19- 912980-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-3 | Trane | 4TWR6036 | 36.8 | MBH | 1200 | CFM | 16.25 | SEER |  |  | Electric | Constant Volume (CV) | N/A
19- 912980-1 | ASHP AHU | Air Source Heat Pump AHU (split system) | HP-4 | Trane | 4TWR6036 | 36.8 | MBH | 1200 | CFM | 16.25 | SEER |  |  | Electric | Constant Volume (CV) | N/A
08- 723130-1 | VRF | Variable Refrigerant Flow | CU-1 | LG | ARUB144BTE4 | 144 | MBH |  |  | 24.2 | IEER |  |  | Electric | N/A | Yes
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-1 | Bryant | 113A-036 | 31.24 | MBH | 1200 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-2 | Bryant | 113A-030 | 25.89 | MBH | 1000 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-3 | Bryant | 113A-036 | 31.24 | MBH | 1200 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-4 | Bryant | 113A-036 | 31.24 | MBH | 1200 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-5 | Bryant | 113A-048 | 42.74 | MBH | 1600 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-6 | Bryant | 113A-048 | 42.74 | MBH | 1600 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-7 | Bryant | 113A-030 | 25.89 | MBH | 1000 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-8 | Bryant | 113A-018 | 16.3 | MBH | 600 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-9 | Bryant | 113A-018 | 16.3 | MBH | 600 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-10 | Bryant | 113A-018 | 16.3 | MBH | 600 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-11 | Bryant | 113A-030 | 25.89 | MBH | 1000 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-12 | Bryant | 113A-024 | 21.52 | MBH | 800 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-13 | Bryant | 113A-024 | 21.52 | MBH | 800 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-14 | Bryant | 113A-024 | 21.52 | MBH | 800 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
12- 456419-1 | DX AHU | Direct Expansion Split System Air Handler | CU-15 | Bryant | 113A-018 | 16.21 | MBH | 600 | CFM | 13 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 614250-1 | VRF | Variable Refrigerant Flow | VRF-HP-1 | LG | ARUM 264DTE5 | 252 | MBH |  |  | 12.5 | EER | 22 | IEER | Electric | N/A | Yes
18- 614250-1 | VRF | Variable Refrigerant Flow | VRF-HP-2 | LG | ARUM 216DTE5 | 206 | MBH |  |  | 11.2 | EER | 24.8 | IEER | Electric | N/A | Yes
18- 614250-1 | VRF | Variable Refrigerant Flow | VRF-HP-3 | LG | ARUM 121DTE5 | 114 | MBH |  |  | 13.1 | EER | 29.6 | IEER | Electric | N/A | Yes
18- 535655-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#1 | Lennox | LGH240H4B | 294.5 | MBH | 8000 | CFM | 12 | EER |  |  | Electric | Variable Volume (VAV) | N/A
18- 535655-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#2 | Lennox | LGH152U4E | 147.6 | MBH | 5000 | CFM | 12.3 | EER |  |  | Electric | Variable Volume (VAV) | N/A
18- 535655-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AC#3 | Lennox | LGH152U4E | 147.6 | MBH | 5000 | CFM | 12.3 | EER |  |  | Electric | Variable Volume (VAV) | N/A
13- 658146-1 [Other] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YZC090 | 77 | MBH | 3000 | CFM | 12.8 | EER | 22.4 | SEER | Electric | Variable Volume (VAV) | N/A
13- 658146-1 [Other] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YZC072 | 64.6 | MBH | 2500 | CFM | 12.6 | EER | 23.2 | SEER | Electric | Variable Volume (VAV) | N/A
13- 658146-1 [Other] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | RF050434 | 502.6 | MBH | 21050 | CFM | 10.7 | EER | 16.4 | SEER | Electric | Variable Volume (VAV) | N/A
13- 658146-1 [Other] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Trane | YZC048 | 39.1 | MBH | 1780 | CFM | 13.3 | EER | 18.5 | SEER | Electric | Variable Volume (VAV) | N/A
19- 820425-1 | VRF | Variable Refrigerant Flow | CU-1 | LG | ARUN121BTE5 | 120000 | Btu/hr |  |  | Unknown |  | N/A |  | Electric | N/A | Yes
19- 820425-1 | VRF | Variable Refrigerant Flow | CU-1 | LG | ARUN121BTE5 | 135000 | Btu/hr |  |  | Unknown |  | N/A |  | Electric | N/A | Unknown
18- 577317-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | York | ZJ102 | 77.3 | MBH | 2975 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 577317-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | York | ZJ102 | 77.3 | MBH | 2975 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 577317-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | York | ZJ102 | 81.6 | MBH | 3400 | CFM | 12 | EER |  |  | Electric | Constant Volume (CV) | N/A
18- 577317-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | York | ZJ078 | 62.9 | MBH | 2600 | CFM | 11.8 | EER |  |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Trane | YSD150 | 125.1 | MBH | 5000 | CFM | 11.5 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Trane | YSD150 | 125.1 | MBH | 5000 | CFM | 11.5 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Trane | YSD150 | 125.1 | MBH | 5000 | CFM | 11.5 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Trane | YSD150 | 125.1 | MBH | 5000 | CFM | 11.5 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-5 | Trane | YSD150 | 125.1 | MBH | 5000 | CFM | 11.5 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-6 | Trane | YSD150 | 125.1 | MBH | 5000 | CFM | 11.5 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-7 | Trane | YSD090 | 71.7 | MBH | 3000 | CFM | 11 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-8 | Trane | YSD090 | 71.7 | MBH | 3000 | CFM | 11 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-9 | Trane | YSD072 | 57.5 | MBH | 2400 | CFM | 11 | EER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-10 | Trane | YSD036 | 32.5 | MBH | 1200 | CFM | 13 | SEER | N/a |  | Electric | Constant Volume (CV) | N/A
17- 799406-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-11 | Trane | YSD036 | 32.5 | MBH | 1200 | CFM | 13 | SEER | N/a |  | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-1 | York | ZYG05E2B1AA2B111A2 | 4.3 | Tons | 1400 | CFM | 15.4 | SEER | N/A |  | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-2 | York | ZYG08E2B3AA2B111A2 | 7.8 | Tons | 2700 | CFM | 12 | EER | 14 | IEER | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-3 | York | ZYG08E2B3AA2B111A2 | 7.8 | Tons | 2250 | CFM | 12 | EER | 14 | IEER | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-6 | York | ZF180N30R2D1EAA1A1 | 14.4 | Tons | 7000 | CFM | 10.8 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-7 | York | ZF180N30R2D1EAA1A1 | 14.4 | Tons | 7000 | CFM | 10.8 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-8 | York | ZF180N30R2D1EAA1A1 | 14.4 | Tons | 7000 | CFM | 10.8 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
18- 563561-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | G-RTU-9 | York | ZF180N30R2D1EAA1A1 | 14.4 | Tons | 7000 | CFM | 10.8 | EER | 13 | IEER | Electric | Constant Volume (CV) | N/A
17- 551538-3 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Lennox | LGH180H4M | 182.6 | MBH | 6000 | CFM | Unknown |  | N/A |  | Electric | Constant Volume (CV) | N/A
17- 551538-3 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Lennox | LGH092H4M | 92.3 | MBH | 3000 | CFM | Unknown |  | N/A |  | Electric | Constant Volume (CV) | N/A
17- 701880-1 | VRF | Variable Refrigerant Flow | CU-01 | Daikin | RELQ192TATJU | 177.6 | MBH |  |  | 22.1 | IEER |  |  | Electric | N/A | Yes
18- 863366-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48HCF09A | 95.6 | MBH | 3400 | CFM | 12 | EER | 13 | IEER | Electric | 2-Speed | N/A
18- 863366-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48HCF09A | 95.6 | MBH | 3400 | CFM | 12 | EER | 13 | IEER | Electric | 2-Speed | N/A
18- 863366-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48FCF06A | 54 | MBH | 2000 | CFM | 14 | SEER | N/A |  | Electric | 2-Speed | N/A
14- 689118-1 | VRF | Variable Refrigerant Flow | CU-1 | Daikin | REYQ336TTJU | 336 | MBH |  |  | 19 | IEER | 10.7 | EER | Electric | N/A | Yes
14- 689118-1 | VRF | Variable Refrigerant Flow | CU-2 | Daikin | REYQ288TTJU | 288 | MBH |  |  | 21.4 | IEER | 11.8 | EER | Electric | N/A | Yes
14- 689118-1 | VRF | Variable Refrigerant Flow | CU-3 | Daikin | REYQ144TTJU | 144 | MBH |  |  | 24.2 | IEER | 12.9 | EER | Electric | N/A | Yes
14- 689118-1 | VRF | Variable Refrigerant Flow | CU-4 | Daikin | REYQ144TTJU | 144 | MBH |  |  | 24.2 | IEER | 12.9 | EER | Electric | N/A | Yes
17- 550764-1 | DHP | Ductless Heat Pump | ACCU-401 | Mitsubishi | PEAD/PUZ | 36 | MBH |  |  | 19.1 | SEER | 12 | EER | Electric | N/A | N/A
17- 550764-1 | DHP | Ductless Heat Pump | ACCU-402 | Mitsubishi | PEAD/PUZ | 24 | MBH |  |  | 19.6 | SEER | 11.7 | EER | Electric | N/A | N/A
17- 550764-1 | DHP | Ductless Heat Pump | ACCU-403 | Mitsubishi | PEAD/PUZ | 42 | MBH |  |  | 19.1 | SEER | 12 | EER | Electric | N/A | N/A
17- 550764-1 | DHP | Ductless Heat Pump | ACCU-407 | Mitsubishi | PEAD/PUZ | 18 | MBH |  |  | 19.9 | SEER | 10.8 | EER | Electric | N/A | N/A
15- 568036-2 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-1 | Carrier | 48TCTA07 | 65.48 | MBH | 2220 | CFM | 11 | EER | 11.2 | IEER | Electric | Constant Volume (CV) | N/A
15- 568036-2 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-2 | Carrier | 48TCTA07 | 65.48 | MBH | 2220 | CFM | 11 | EER | 11.2 | IEER | Electric | Constant Volume (CV) | N/A
15- 568036-2 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-3 | Carrier | 48TCTA07 | 65.48 | MBH | 2220 | CFM | 11 | EER | 11.2 | IEER | Electric | Constant Volume (CV) | N/A
15- 568036-2 | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU-4 | Carrier | 48TCTA07 | 65.48 | MBH | 2220 | CFM | 11 | EER | 11.2 | IEER | Electric | Constant Volume (CV) | N/A
19- 550436-1 | VRF | Variable Refrigerant Flow | CU-1 | Mitsubishi | PURY-HP192TSKMU-A-H | 15.3 | Tons |  |  | 12.1 | EER | 16.6 | IEER | Electric | N/A | No
19- 550436-1 | VRF | Variable Refrigerant Flow | CU-2 | Mitsubishi | PURY-HP192TSKMU-A-H | 15.7 | Tons |  |  | 12.1 | EER | 16.6 | IEER | Electric | N/A | No
13- 658146-1 [Natatorium] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU R.1 | Trane | YZC090 | 81.9 | MBH | 3000 | CFM | 12.8 | EER | 22.4 | SEER | Electric | Constant Volume (CV) | N/A
13- 658146-1 [Natatorium] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU R.2 | Trane | YZC072 | 72.9 | MBH | 2500 | CFM | 12.6 | EER | 23.2 | SEER | Electric | Constant Volume (CV) | N/A
13- 658146-1 [Natatorium] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU R.3 | Trane | RF050434 | 636 | MBH | 21050 | CFM | 10.7 | EER | 16.4 | SEER | Electric | Constant Volume (CV) | N/A
13- 658146-1 [Natatorium] | DX RTU | Direct Expansion Packaged Rooftop HVAC | RTU R.4 | Trane | YZC048 | 39.1 | MBH | 1780 | CFM | 13.3 | EER | 18.5 | SEER | Electric | Constant Volume (CV) | N/A
18- 559771-1 | DHP | Ductless Heat Pump | DSS-1 | Mitsubishi | SUZ-KA15NA | 15000 | Btu/hr |  |  | 16 | SEER | N/A |  | Electric | N/A | N/A
11- 556107-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AHU-1 | AAON | RN-060-3-0-EA09-3D9 | 695 | MBH | 22000 | CFM | 10.4 | EER | 12.1 | IEER | Electric | Variable Volume (VAV) | N/A
11- 556107-1 | DX RTU | Direct Expansion Packaged Rooftop HVAC | AHU-1 | AAON | RN-060-3-0-EA09-3D9 | 695 | MBH | 22000 | CFM | 10.4 | EER | 12.1 | IEER | Electric | Variable Volume (VAV) | N/A

## Stage2SuppHVAC
Project_ID | Long Description | Equipment ID | Cooling Capacity | Capacity_Metric_1_Units | Cooling Efficiency | Efficiency_Metric_1_Units | Cooling Eff2 | Efficiency_Metric_2 | Heating Capacity | Heating_Capacity_Metric | Heating Efficiency | Efficiency_Metric_Units | Efficiency_2 | Efficiency_Metric_2_Units | Heating Fuel Type | Cooling Fuel Type | Includes_AuxElecCoils | AuxElecCoil_Cap | Notes_SuppHVAC
07- 782313-1 | Ductless Air Conditioner | AC-B05 | 30 | MBH | 15.5 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi PKA-A30, PUY-A30; serves elevator machine room
07- 782313-1 | Electric Zonal | EH-1 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | Electric radiant heater
07- 782313-1 | Electric Zonal | EH-3 | [6 empty] | 7 | kW |  |  |  |  | Electric |  | N/A |  | Electric unit heater
07- 782313-1 | Electric Zonal | EH-4 | [6 empty] | 3.3 | kW |  |  |  |  | Electric |  | N/A |  | Electric unit heater
07- 782313-1 | Electric Zonal | EH-6 | [6 empty] | 375 | Watts |  |  |  |  | Electric |  | N/A |  | Electric radiant ceiling panel
09- 581175-1 | Ductless Heat Pump | ODU-1 | 12000 | Btu/hr | 18 | SEER |  |  | 12200 | Btu/hr | 8.5 | HSPF |  |  | Electric | Electric | No |  | Mitsubishi MUZ-HE12NA
09- 581175-1 | Gas Zonal | UH-1 | [6 empty] | 200 | MBH | 83 | % |  |  | Natural Gas |  | N/A |  | Reznor UDAS-200
09- 581175-1 | Electric Zonal | EUH-4 | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A |  | KING WHF
09- 581175-1 | Electric Zonal | EUH-5 | [6 empty] | 2400 | Watts |  |  |  |  | Electric |  | N/A |  | KING WHF
09- 581175-1 | Electric Zonal | EUH-6 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A |  | KING WHF
09- 581175-1 | Electric Zonal | EUH-7 | [6 empty] | 2000 | Watts |  |  |  |  | Electric |  | N/A |  | KING KBP
11- 631833-2 | Ductless Air Conditioner | CU-6 | 24000 | Btu/hr | 13.4 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi PUZ A 24NHA BS
11- 631833-2 | Ductless Air Conditioner | CU-7 | 12000 | Btu/hr | 13 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi PUZ-A12NHA-BS
11- 656138-1 | Ductless Air Conditioner | MCU-1 | 22000 | Btu/hr | 21.5 | SEER | [9 empty] | Electric | N/A |  | LG LSN243HLV; 800 CFM
11- 656138-1 | Electric Zonal | EWH-1 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Wall mounted electric heater; BROAN 198
12- 701660-1 | Electric Zonal | EUH-5 | [6 empty] | 7.5 | kW |  |  |  |  | Electric |  | N/A
12- 701660-1 | Electric Zonal | EWH-6 | [6 empty] | 0.75 | kW |  |  |  |  | Electric |  | N/A
12- 701660-1 | Electric Zonal | EWH-7 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
12- 701660-1 | Electric Zonal | EUH-8 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
12- 701660-1 | Electric Zonal | EWH-9 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
13- 404186-1 | Ductless Air Conditioner | CU-R-1 | 24 | MBH | 16.5 | SEER | [9 empty] | Electric | N/A |  | Daikin RZR24PVJU; serves elevator control room
13- 404186-1 | Electric Zonal | EHC-4-1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Electric Duct Heater
13- 404186-1 | Electric Zonal | EUH-B-1 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater
13- 404186-1 | Electric Zonal | EUH-B-2 | [6 empty] | 12 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater
13- 404186-1 | Electric Zonal | EUH-1-1 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater
13- 636582-1 | Ductless Heat Pump | DS-3 | 24.3 | MBH | 17.9 | SEER |  |  | 19.45 | MBH | 8.3 | HSPF |  |  | Electric | Electric | No
14- 426751-1 | Gas Zonal | GRH-3 | [6 empty] | 80 | MBH | 92 | % |  |  | Natural Gas |  | N/A |  | Gas Radiant Heater - Output assumed based on 92% of 80 MBH Input
14- 493663-2 | Electric Zonal | EWH-P101 | [6 empty] | 4800 | Watts |  |  |  |  | Electric |  | N/A
14- 493663-2 | Electric Zonal | EWH-P108 | [6 empty] | 2250 | Watts |  |  |  |  | Electric |  | N/A
14- 493663-2 | Electric Zonal | EWH-B101 | [6 empty] | 4000 | Watts |  |  |  |  | Electric |  | N/A
14- 493663-2 | Electric Zonal | EWH-R100 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A
14- 493663-2 | Electric Zonal | EUH-B110 | [6 empty] | 5000 | Watts |  |  |  |  | Electric |  | N/A |  | Quantity: 4
14- 494803-1 | Ductless Heat Pump | DSS-1 | 9000 | Btu/hr | 30.5 | SEER |  |  | 10900 | Btu/hr | 13.5 | HSPF |  |  | Electric | Electric | No |  | Mitsubishi MUZ-FH09NA
14- 494803-1 | Ductless Heat Pump | DSS-2 | 24000 | Btu/hr | 17 | SEER |  |  | 26000 | Btu/hr | 10.8 | HSPF |  |  | Electric | Electric | No |  | Mitsubishi PUZ-A24NHA4
14- 494803-1 | Ductless Heat Pump | DSS-3 | 18000 | Btu/hr | 15.3 | SEER |  |  | 19000 | Btu/hr | 9.5 | HSPF |  |  | Electric | Electric | No |  | Mitsubishi PUZ-A18NHA4
14- 494803-1 | Electric Zonal | WH-1 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A |  | Broan 170; electric wall heater
14- 494803-1 | Electric Zonal | WH-2 | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A |  | Broan 170; electric wall heater
14- 494803-1 | Electric Zonal | WH-3 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A |  | Broan 170; electric wall heater
14- 494803-1 | Gas Zonal | GH-1 | [6 empty] | 200 | MBH | 83 | % |  |  | Natural Gas |  | N/A |  | Reznor UDAP-200; gas unit heater; 0.25 hp fan
14- 526453-1 [DHP] | Ductless Air Conditioner | CU-3 | 17.2 | MBH | 19.2 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi MUY-GE18NA-1
18- 595441 | Electric Zonal | EH-102 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | Electric heater, no cooling
14- 540112-1 [Corridors\Main Floor Areas] | Air Source Heat Pump (Split System) | CU-2 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Carrier 25HHA448
14- 540112-1 [Misc.] | Electric Zonal | EDH-1 | [6 empty] | 13 | kW |  |  |  |  | Electric |  | N/A |  | Warren Technology CBK
14- 540112-1 [Misc.] | Electric Zonal | EH-1 | [6 empty] | 2.2 | kW |  |  |  |  | Electric |  | N/A |  | King PAW2022
14- 550027-2 | Gas Zonal | UH-T | [6 empty] | 60 | MBH | 83 | % |  |  | Natural Gas |  | N/A
14- 550027-2 | Ductless Air Conditioner | AC-1.5 | 1.5 | Tons | 14 | SEER | [9 empty] | Electric | N/A
14- 550027-2 | Electric Zonal | DH-P | [6 empty] | 20 | kW |  |  |  |  | Electric |  | N/A |  | WARREN
14- 550027-2 | Gas Zonal | RH-1 | [6 empty] | 34 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | Sunpak TSR
14- 550027-2 | Direct Expansion Packaged Rooftop HVAC | RTU-2 | 4 | Tons | 14 | SEER |  |  | 72 | MBH | 0.8 |  |  |  | Electric | Electric | No |  | CARRIER 48TCD05
14- 550027-2 | Direct Expansion Packaged Rooftop HVAC | RTU-3 | 8.5 | Tons | 11 | EER |  |  | 180 | MBH | 0.8 |  |  |  | Electric | Electric | No |  | CARRIER 48TCE09
14- 673795-2 | Electric Zonal | EWH-4 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A
14- 673795-2 | Electric Zonal | EWH-5 | [6 empty] | 0.75 | kW |  |  |  |  | Electric |  | N/A
14- 673795-2 | Electric Zonal | EWH-6 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
14- 673795-2 | Electric Zonal | EWH-7 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
14- 673795-2 | Electric Zonal | EWH-8 | [6 empty] | 3.2 | kW |  |  |  |  | Electric |  | N/A
14- 587282-1 | Electric Zonal | EH-006 | [6 empty] | Unknown | [5 empty] | Electric |  | N/A |  | No capacity listed for EH-006
14- 611061-1 | Ductless Heat Pump | HP-1B | 1 | Tons | 19 | SEER |  |  | 13.5 | MBH | 9 | HSPF |  |  | Electric | Electric | No |  | Serves Elevator Equipment Room
14- 626014-1 | Ductless Air Conditioner | CU-2 | 10.9 | MBH | 15 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi MUY-GE09NA
14- 626014-1 | Ductless Air Conditioner | CU-3 | 12 | MBH | 20.5 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi MUY-GE12NA
14- 626014-1 | Ductless Air Conditioner | CU-14 | 25.5 | MBH | [11 empty] | Electric | N/A |  | Desert Aire RC5S018C; serves pool room
14- 626014-1 | Packaged Terminal Heat Pump | PTHP-1 | 7 | MBH | 13 | SEER |  |  | 5.8 | MBH | 3.6 | HSPF |  |  | Electric | Electric | No |  | Friedich PDH07K
14- 626014-1 | Packaged Terminal Heat Pump | PTHP-2 | 9.2 | MBH | 12.1 | SEER |  |  | 8.1 | MBH | 3.5 | HSPF |  |  | Electric | Electric | No |  | Friedich PDH09K
14- 626014-1 | Packaged Terminal Heat Pump | PTHP-3 | 11.6 | MBH | 11.6 | SEER |  |  | 10.4 | MBH | 3.4 | HSPF |  |  | Electric | Electric | No |  | Friedich PDH12K
14- 626014-1 | Packaged Terminal Heat Pump | PTHP-4 | 14.2 | MBH | 10.4 | SEER |  |  | 13 | MBH | 3.1 | HSPF |  |  | Electric | Electric | No |  | Friedich PDH15K
14- 626014-1 | Electric Zonal | DH-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Thermolec NER-12-5-208/1
14- 626014-1 | Electric Zonal | DH-2 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Thermolec NER-10-5-208/1
14- 626014-1 | Air Source Heat Pump (Packaged) | AHU-2 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | York ZF150
14- 634379-1 | Electric Zonal | UH-4 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Q-Mark MUH-03-81; serves exit hallway-106; fan hp 0.1
14- 634379-1 | Gas Zonal | UH-3 | [6 empty] | 145000 | Btu/hr | 80 | % |  |  | Natural Gas |  | N/A |  | Lennox LF24-145A; serves receiving area; fan hp 0.125
14- 662676-1 | Ductless Heat Pump | AC-1 | 18 | MBH | 15.3 | SEER |  |  | 13 | MBH | 9.5 | HSPF |  |  | Electric | Electric | Unknown |  | Mitsubishi PKA-A18HA4; serves elevator machine room; fan motor HP 0.33
14- 662676-1 | Electric Zonal | EWH-1 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A |  | King PAW2022; serves sprinkler closet
14- 731874-1 [VRF] | Ductless Air Conditioner | CU-1 | 10 | MBH | 19 | SEER | 12.5 | EER | [7 empty] | Electric | N/A
14- 731874-1 [VRF] | Ductless Heat Pump | HP-4 | 18 | MBH | 17.5 | SEER | 14.1 | EER | 20 | MBH | 10.6 | HSPF |  |  | Electric | Electric | No | N/A
15- 411092-1 | Electric Zonal | SPUH-1 | [6 empty] | 7.5 | kW |  |  |  |  | Electric |  | N/A
15- 411092-1 | Gas Zonal | ACUH-3 | [6 empty] | 100 | MBH | Unknown |  |  |  | Natural Gas |  | N/A
15- 411092-1 | Gas Zonal | VUH-2 | [6 empty] | 250 | MBH | Unknown |  |  |  | Natural Gas |  | N/A
15- 411092-1 | Gas Zonal | VRH-1 | [6 empty] | 150 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | This is a gas radiant heater
15- 411092-1 | Gas Zonal | VRH-2 | [6 empty] | 80 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | This is a gas radiant heater
15- 419460-1 | Ductless Heat Pump | CU-4 | 35 | MBH | 14.2 | SEER |  |  | 34.4 | MBH | 3.5 | COP(47) |  |  | Electric | Electric | No
15- 419460-1 | Electric Zonal | EBH-2 | [6 empty] | 1.2 | kW |  |  |  |  | Electric |  | N/A
15- 425673-1 | Electric Zonal | EUH-8 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | QMARK MUH; serves turnout 134
15- 425673-1 | Gas Zonal | IH-4 | [6 empty] | 60 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | Roberts Gordon CRV B-6
15- 427602-1 | Electric Zonal | WH-1 | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A
15- 427602-1 | Ductless Air Conditioner | DSCU-2 | 12000 | BTU/hr | 19 | SEER | [9 empty] | Electric | N/A
15- 458201-1 | Packaged Terminal Heat Pump | VT-A | 8.9 | MBH | 9 | EER |  |  | 8.5 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3 kW
15- 458201-1 | Packaged Terminal Heat Pump | VT-B | 11.4 | MBH | 9.1 | EER |  |  | 11.5 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3.8
15- 458201-1 | Packaged Terminal Heat Pump | VT-C | 17.4 | MBH | 9 | EER |  |  | 16.7 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 4.5
15- 458201-1 | Ductless Air Conditioner | AC-2 | 36 | MBH | 14 | SEER | [9 empty] | Electric | N/A
15- 458201-1 | Electric Zonal | EH-8 | [6 empty] | 6 | kW |  |  |  |  | Electric |  | N/A
15- 458201-1 | Electric Zonal | EH-10 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
15- 458201-1 | Electric Zonal | EH-13 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
15- 458201-1 | Electric Zonal | EH-14 | [6 empty] | 0.75 | kW |  |  |  |  | Electric |  | N/A
15- 458201-1 | Other Rooftop HVAC | F-2 | 24 | MBH | Unknown |  |  |  | 35 | MBH | 95 | % |  |  | Natural Gas | Electric | N/A
15- 458201-1 | Other Rooftop HVAC | F-3 | 18 | MBH | Unknown |  |  |  | 9.9 | MBH | 95 | % |  |  | Natural Gas | Electric | N/A
15- 458201-1 | Other Rooftop HVAC | F-4 | 30 | MBH | Unknown |  |  |  | 22 | MBH | 95 | % |  |  | Natural Gas | Electric | N/A
15- 464466-1 | Electric Zonal | DH-1 | [6 empty] | 30 | kW |  |  |  |  | Electric |  | N/A |  | Electric heater for the restaurant portion
15- 464466-1 | Gas Heat/Direct Expansion Rooftop HVAC | ACCU-2 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Air cooled condensing unit
15- 464466-1 | Electric Zonal | EH-1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
15- 464466-1 | Electric Zonal | DH-1(ERV-1) | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A
15- 464466-1 | Electric Zonal | DH-2(FV-1) | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
15- 464466-1 | Gas Zonal | FU-1 | [6 empty] | 88.5 | MBH | 80 | % |  |  | Natural Gas |  | N/A |  | Calculated efficiency
15- 464466-1 | Gas Zonal | FU-2 | [6 empty] | 175 | MBH | 80 | % |  |  | Natural Gas |  | N/A |  | Calculated efficiency
15- 472299-1 | Ductless Heat Pump | HP-10 | 15 | MBH | 16 | SEER | 16 | EER | 18 | MBH | 2.71 | COP(47) |  |  | Electric | Electric | No
15- 472299-1 | Air Source Heat Pump (Split System) | CU-3 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Cooling - 17.2 MBH, SEER/EER 17.2, No heating
15- 589031-1 | Electric Zonal | EUH-1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
03- 779006-1 | Electric Zonal | EH-1 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A |  | Electric wall heater; QMARK CWH1151DSF
15- 692220-1 | Electric Zonal | UH-1 | [6 empty] | 0.5 | kW |  |  |  |  | Electric |  | N/A
15- 692220-1 | Electric Zonal | ECH-1 | [6 empty] | 600 | Watts |  |  |  |  | Electric |  | N/A
15- 692220-1 | Electric Zonal | ECH-2 | [6 empty] | 450 | Watts |  |  |  |  | Electric |  | N/A
15- 700290-1 | Electric Zonal | EH-1 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
16- 400924-1 | Air Source Heat Pump (Split System) | MS-4B | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown
16- 403736-1 | Electric Zonal | DH-1 | [6 empty] | 4.5 | kW |  |  |  |  | Electric |  | N/A
16- 404663-1 | Ductless Heat Pump | AC-1 | 19.1 | MBH | 23.5 | SEER |  |  | 15.5 | MBH | 12 | HSPF |  |  | Electric | Electric | No
16- 404663-1 | Electric Zonal | EH-5 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
16- 404663-1 | Electric Zonal | EH-8 | [6 empty] | 4.8 | kW |  |  |  |  | Electric |  | N/A
16- 404663-1 | Electric Zonal | EH-10 | [6 empty] | 0.5 | kW |  |  |  |  | Electric |  | N/A
16- 404663-1 | Ductless Air Conditioner | AC-3 | 17 | MBH | 18.5 | SEER | [9 empty] | Electric | N/A
16- 404663-1 | Packaged Terminal Air Conditioner | PTAC-1 | 9.5 | MBH |  |  | 12.9 | EER | [7 empty] | Electric | No
16- 423218-1 | Ductless Heat Pump | FC-1 | 29.5 | MBH |  |  |  |  | 36 | MBH |  |  |  |  | Electric | Electric | Yes | 10 kW
16- 423218-1 | Ductless Heat Pump | FC-2 | 32.8 | MBH |  |  |  |  | 36 | MBH |  |  |  |  | Electric | Electric | Yes | 10 kW
16- 423218-1 | Ductless Air Conditioner | DFC-1 | 18000 | Btu/hr | 14.1 | SEER | [9 empty] | Electric | N/A
16- 423218-1 | Electric Zonal | EUH-1 | [6 empty] | 1900 | Watts |  |  |  |  | Electric |  | N/A
16- 423218-1 | Electric Zonal | EWH-6 | [6 empty] | 3000 | Watts |  |  |  |  | Electric |  | N/A
16- 423218-1 | Electric Zonal | EWH-5 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A
16- 490400-1 | Ductless Air Conditioner | DSS-5 | 36000 | Btu/hr | 18.8 | SEER | 10.8 | EER | [7 empty] | Electric | N/A |  | Mitsubishi PUY-A36NKA7/PKA-A36KA7
16- 490400-1 | Electric Zonal | DH-1 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A |  | Electric duct heater; Brasch open coil
14- 730160-1 | Electric Zonal | BB 2 | [6 empty] | 1172 | Watts |  |  |  |  | Electric |  | N/A |  | Base Board Wall Heater
14- 730160-1 | Standalone Fans (0-1HP) | EF 1 | 1 | Fans | [10 empty] | Electric | Electric |  |  | HVAC Fan Schedule
14- 730160-1 | Ductless Air Conditioner | DAC 3 | 42 | MBH | Unknown | [10 empty] | Electric | N/A |  | Ductless Split System AC Unit, no Cooling Efficiency listed nor list of space it serves
14- 730160-1 | Ductless Heat Pump | DCU 3 | 3.5 | Tons | 16 | SEER |  |  | Unknown | [5 empty] | Electric | Electric | No | N/A | Ductless Split System Condensing Unit, Only lists SEER and Capacity
14- 730160-1 | Electric Zonal | UH 2 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater, No Cooling
14- 730160-1 | Electric Zonal | UH 4 | [6 empty] | 25 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater, No Cooling
15- 419203-1 [Additional Areas] | Ductless Air Conditioner | OAC-1 | 48000 | Btu/hr | 15.1 | IEER | [9 empty] | Electric | N/A
15- 419203-1 [Additional Areas] | Electric Zonal | EUH-3 | [6 empty] | 7.5 | kW |  |  |  |  | Electric |  | N/A |  | Electric unit heater
15- 419203-1 [Additional Areas] | Electric Zonal | EUH-4 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Electric unit heater
15- 419203-1 [Additional Areas] | Electric Zonal | EWH-2 | [6 empty] | 2000 | Watts |  |  |  |  | Electric |  | N/A |  | Electric wall heater
16- 514976-1 | Ductless Heat Pump | HP2 | 24000 | Btu/hr | 17.3 | SEER |  |  | 27600 | Btu/hr | 9.4 | HSPF |  |  | Electric | Electric | No
16- 514976-1 | Packaged Terminal Heat Pump | PTHP1 | 14900 | Btu/hr | 11.2 | EER |  |  | 13200 | Btu/hr | 3.1 | COP(47) |  |  | Electric | Electric | Yes | 3.1 kW | "Electric Heater (kW)" was assumed to be aux electric
16- 514976-1 | Electric Zonal | EWH2 | [6 empty] | 1710 | Btu/hr |  |  |  |  | Electric |  | N/A
16- 514976-1 | Electric Zonal | EH1 | [6 empty] | 34120 | Btu/hr |  |  |  |  | Electric |  | N/A
16- 514976-1 | Electric Zonal | ECH2 | [6 empty] | 6825 | Btu/hr |  |  |  |  | Electric |  | N/A
16- 514976-1 | Electric Zonal | RWH1 | [6 empty] | 3069 | Btu/hr |  |  |  |  | Electric |  | N/A
16- 514976-1 | Electric Zonal | RWH2 | [6 empty] | 4092 | Btu/hr |  |  |  |  | Electric |  | N/A
16- 536718-1 | Electric Zonal | EH-10 | [6 empty] | 2750 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING LPW2045C
16- 536718-1 | Electric Zonal | EH-19 | [6 empty] | 2250 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING LPW2045C-G
16- 536718-1 | Electric Zonal | EH-21 | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING WHFC1210
16- 536718-1 | Electric Zonal | EH-24 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING LPW1227C-G
16- 536718-1 | Electric Zonal | EH-25 | [6 empty] | 4000 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING LPW2045C-G
16- 536718-1 | Electric Zonal | EH-26 | [6 empty] | 3500 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING LPW2045C-G
16- 536718-1 | Electric Zonal | EH-29 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A |  | Ceiling heater; KING WHFC1210
16- 536718-1 | Electric Zonal | EDH-1 | [6 empty] | 16 | kW |  |  |  |  | Electric |  | N/A |  | Electric duct heater serving Air-to-Air energy recovery ventilator ERV-1
16- 536718-1 | Electric Zonal | EDH-2 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Electric duct heater serving Air-to-Air energy recovery ventilator ERV-2
16- 536718-1 | Electric Zonal | EDH-3 | [6 empty] | 8 | kW |  |  |  |  | Electric |  | N/A |  | Electric duct heater serving Air-to-Air energy recovery ventilator ERV-3
16- 536718-1 | Electric Zonal | EDH-4 | [6 empty] | 40 | kW |  |  |  |  | Electric |  | N/A |  | Electric duct heater serving make-up air unit
16- 536718-1 | Ductless Air Conditioner | SSO-01/SSI-01 | 18 | MBH | 18 | SEER | [9 empty] | Electric | N/A |  | Serves elevator equipment room
16- 536718-1 | Electric Zonal | EUH-3 | [6 empty] | 10 | kW |  |  |  |  | Electric |  | N/A |  | Second floor east wing alt. bid; KING KB-2410-3MP-B2
16- 536718-1 | Packaged Terminal Heat Pump | HP-U | 9 | MBH | 10.5 | EER |  |  | 8.3 | MBH | 3.3 | COP(47) |  |  | Electric | Electric | No |  | Vertical Packaged terminal heat pump; GE Zoneline AZ85H09D
16- 537171-1 | Air Source Heat Pump (Split System) | CU5 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown
16- 537171-1 | Electric Zonal | CH1 | [6 empty] | 900 | Watts |  |  |  |  | Electric |  | N/A
16- 537171-1 | Electric Zonal | CH2 | [6 empty] | 1800 | Watts |  |  |  |  | Electric |  | N/A
16- 537171-1 | Electric Zonal | EUH1-3 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
16- 537171-1 | Electric Zonal | EUH1-5 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
16- 537171-1 | Ductless Heat Pump | CU5 | 22000 | Btu/hr | 12.5 | EER | 20 | SEER | 27600 | Btu/hr | 10.2 | HSPF |  |  | Electric | Electric | No | N/A
16- 572659-1 | Electric Zonal | EH-1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
16- 572659-1 | Electric Zonal | EH-2 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A
16- 572659-1 | Packaged Terminal Air Conditioner | PT-1 | 7.1 | MBH |  |  | 13.3 | EER | [7 empty] | Electric | No
16- 572659-1 | Packaged Terminal Air Conditioner | PT-2 | 9.3 | MBH |  |  | 12.9 | EER | [7 empty] | Electric | No
16- 577162-1 | Electric Zonal | EWH-1 | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A
16- 577162-1 | Air Source Heat Pump (Split System) | DS-1 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Cooling - 15.76 MBH, 13 SEER, 657 CFM
16- 607207-1 | Ductless Heat Pump | HP-1 | 10.9 | MBH | 19 | SEER |  |  | 13.5 | MBH | 9 | HSPF |  |  | Electric | Electric | No
16- 615057-1 | Electric Zonal | EH-3-7 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A |  | Electric Heater, no cooling
16- 615057-1 | Electric Zonal | EH-3-12 | [6 empty] | 2000 | Watts |  |  |  |  | Electric |  | N/A |  | Electric Heater, no cooling
16- 615057-1 | Electric Zonal | EH-6-1 | [6 empty] | 5000 | Watts |  |  |  |  | Electric |  | N/A |  | Electric Heater, no cooling
16- 615057-1 | Electric Zonal | EH-10-1 | [6 empty] | 3000 | Watts |  |  |  |  | Electric |  | N/A |  | Electric Heater, no cooling
16- 615057-1 | Air Source Heat Pump (Split System) | HP-C-1 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Elevator Split System Heat Pump
16- 640402-1 | Gas Zonal | AHU-1 | [6 empty] | 66 | MBH | 97 | AFUE |  |  | Natural Gas |  | N/A |  | Armstrong A97DSMV070B12S; serves corridor; includes cooling coil from outdoor condensing unit/heat pump CU-1
16- 640402-1 | Ductless Air Conditioner | CU-1 | 34 | MBH | 14 | SEER | [9 empty] | Electric | N/A |  | Armstrong 4SCU14LE136P-4A; serves corridor, cooling only coil located in gas furnace AHU-1
15- 573278-1 | Ductless Air Conditioner | AC-4 | 24 | MBH | 17 | SEER | [9 empty] | Electric | N/A
15- 573278-1 | Ductless Air Conditioner | AC-5 | 10 | MBH | 18 | SEER | [9 empty] | Electric | N/A
15- 573278-1 | Electric Zonal | EH-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
16- 657491-1 | Ductless Air Conditioner | DS-0.1 | 9 | MBH | 15 | SEER | [9 empty] | Electric | N/A |  | No heating
16- 662436-1 | Ductless Heat Pump | HP-1 | 42.2 | MBH | 14 | SEER |  |  | 10.8 kW |  | 8.2 | HSPF |  |  | Electric | Electric | No |  | Trane 4TWR4048
16- 662436-1 | Ductless Heat Pump | HP-2 | 24.6 | MBH | 14.5 | SEER |  |  | 5.76 kW |  | 8.5 | HSPF |  |  | Electric | Electric | No |  | Trane 4TWR4030
16- 662436-1 | Ductless Heat Pump | HP-3 | 15.8 | MBH | 14.5 | SEER |  |  | 3.6 kW |  | 8.5 | HSPF |  |  | Electric | Electric | No |  | Trane 4TWR4018
16- 662436-1 | Packaged Terminal Heat Pump | PTHP-1 | 12 | MBH | 10.7 | EER |  |  | 2.5 kW |  | 3.2 | COP(47) |  |  | Electric | Electric | No |  | Amana PTH123G25
16- 662436-1 | Electric Zonal | EH-1 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | Q-Mark CZ1012T
16- 662436-1 | Electric Zonal | EH-2 | [6 empty] | 1.125 | kW |  |  |  |  | Electric |  | N/A |  | Q-Mark QTS1100
16- 662436-1 | Electric Zonal | EH-3 | [6 empty] | 2.4 | kW |  |  |  |  | Electric |  | N/A |  | Greenheck IDHC
16- 680124-1 | Electric Zonal | EWH-1 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A
16- 680124-1 | Gas Zonal | UH-2 | [6 empty] | 100 | MBH | 80 | % |  |  | Natural Gas |  | N/A
16- 680124-1 | Ductless Air Conditioner | CU-1 | 11200 | Btu/hr | 21.5 | SEER | [9 empty] | Electric | N/A
16- 688717-1 [VRF] | Electric Zonal | EWH-1 | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A
16- 688717-1 [VRF] | Electric Zonal | EWH-3 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A
16- 688717-1 [VRF] | Electric Zonal | EWH-4 | [6 empty] | 2250 | Watts |  |  |  |  | Electric |  | N/A
16- 688717-1 [VRF] | Electric Zonal | EWH-5 | [6 empty] | 3000 | Watts |  |  |  |  | Electric |  | N/A
16- 688717-1 [VRF] | Electric Zonal | EWH-1 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A
16- 688717-1 [VRF] | Electric Zonal | EWH-2 | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A
16- 688717-1 [VRF] | Ductless Air Conditioner | DS-5 | 12 | MBH | 16.5 | SEER | 10.8 | EER | [7 empty] | Electric | N/A |  | space served Unknown
16- 688717-1 [VRF] | Ductless Heat Pump | DS-4 | 18.2 | MBH | 20.5 | SEER | 12.6 | EER | 22 | MBH | Unknown |  |  |  | Electric | Electric | No | N/A
16- 706094-1 | Ductless Air Conditioner | AC-702-B | 30 | MBH | [11 empty] | Electric | N/A |  | Efficiency is noted at "ARI standard conditions"
16- 706094-1 | Ductless Air Conditioner | AC-703 | 24 | MBH | [11 empty] | Electric | N/A |  | Efficiency is noted at "ARI standard conditions"
16- 706094-1 | Electric Zonal | UH-701 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
16- 706094-1 | Other Rooftop HVAC | DH-601 | Unknown |  | Unknown |  |  |  | 4 | kW | 1 | COP |  |  | Electric |  | N/A |  | 4 kW Duct Heater
16- 720532-1 | Electric Zonal | WH#1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | 175 CFM; Electric wall heater; Markel HF3324TTD-RP
16- 727455-1 | Other Rooftop HVAC | AHU-1 | 72 | MBH | 15 | EER |  |  | 96 | MBH | 80 | % |  |  | Natural Gas | Electric | N/A |  | Air Handling Unit serving commercial kitchen
16- 727455-1 | Gas Heat/Direct Expansion Rooftop HVAC | CU-3 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Air source condenser + Dx AC unit
16- 727455-1 | Electric Zonal | EWH-8 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
16- 727455-1 | Electric Zonal | EWH-12 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A
16- 727455-1 | Electric Zonal | EBH-2 | [6 empty] | 1.2 | kW |  |  |  |  | Electric |  | N/A
16- 727455-1 | Gas Zonal | UH-1 | [6 empty] | 30 | MBH | 80 | % |  |  | Natural Gas |  | N/A
16- 727455-1 | Electric Zonal | ECH-11 | [6 empty] | 900 | Watts |  |  |  |  | Electric |  | N/A
16- 727455-1 | Electric Zonal | ECH-13 | [6 empty] | 450 | Watts |  |  |  |  | Electric |  | N/A
16- 727455-1 | Packaged Terminal Heat Pump | PTHP-1 | 6.7 | MBH | 12 | EER |  |  | 6.2 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 2.3 kW
16- 727455-1 | Packaged Terminal Heat Pump | PTHP-2 | 9.2 | MBH | 11.5 | EER |  |  | 8 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3.2 kW
16- 727455-1 | Packaged Terminal Heat Pump | PTHP-3 | 11.5 | MBH | 11.2 | EER |  |  | 10.6 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3.2 kW
16- 727455-1 | Packaged Terminal Heat Pump | VTHP-2B2 | 17.2 | MBH | 10 | EER |  |  | 15.5 | MBH | 2.5 | COP(47) |  |  | Electric | Electric | Yes | 3.2 kW
15- 640275-1 [Common Areas and Corridors] | Electric Zonal | EH-1 | [6 empty] | 450 | Watts |  |  |  |  | Electric |  | N/A
15- 640275-1 [Common Areas and Corridors] | Electric Zonal | EH-2 | [6 empty] | 4000 | Watts |  |  |  |  | Electric |  | N/A
15- 640275-1 [Common Areas and Corridors] | Electric Zonal | EH-3 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A
15- 640275-1 [Common Areas and Corridors] | Electric Zonal | DH-1 | [6 empty] | 20 | kW |  |  |  |  | Electric |  | N/A |  | Inline duct heater
15- 640275-1 [Common Areas and Corridors] | Electric Zonal | DH-2 | [6 empty] | 8 | kW |  |  |  |  | Electric |  | N/A |  | Inline duct heater
16- 429395-1 | Packaged Terminal Heat Pump | PTAC-1 | 1 | Tons | 11 | EER |  |  | 2.1 kW |  | 3.2 | COP(47) |  |  | Electric | Electric | Unknown |  | Amana PTH 123G
16- 429395-1 | Ductless Air Conditioner | CU-1 | 18 | MBH | 15 | SEER | 10.4 | EER | [7 empty] | Electric | N/A |  | Daikin RXN09NMVJU; serves equipment room
17- 521675-1 | Gas Heat/Direct Expansion Rooftop HVAC | RTU-2 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | serves corridors
17- 521675-1 | Electric Zonal | EUH P1-3 | [6 empty] | 3.3 | kW |  |  |  |  | Electric |  | N/A
17- 521675-1 | Electric Zonal | EUH 1-3 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
17- 521675-1 | Electric Zonal | EWH 1-5 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A
17- 521675-1 | Electric Zonal | ECH 6-1 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
17- 521675-1 | Ductless Air Conditioner | HP 6-2 | 18000 | Btu/hr | [11 empty] | Electric | N/A |  | L6 AV Room
17- 521675-1 | Ductless Air Conditioner | AC R-1 | 36000 | Btu/hr | [11 empty] | Electric | N/A |  | Generator R700
17- 571695-2 | Ductless Heat Pump | CU-2 | 18000 | Btu/hr | 15.3 | SEER |  |  | 19000 | Btu/hr | 9.5 | HSPF |  |  | Electric | Electric | No |  | Mitsubishi PUZ-A18NHA4; serves IT room level 2
17- 584823-1 | Ductless Air Conditioner | AC-G-01 | 24000 | Btu/hr | 18 | SEER | 12.5 | EER | [7 empty] | Electric | N/A
17- 584823-1 | Ductless Air Conditioner | AC-G-02 | 36000 | Btu/hr | 15.9 | SEER | 9.1 | EER | [7 empty] | Electric | N/A
17- 584823-1 | Ductless Air Conditioner | AC-G-03 | 12000 | Btu/hr | 19 | SEER | 12.5 | EER | [7 empty] | Electric | N/A
17- 584823-1 | Ductless Air Conditioner | AC-3-01 | 18000 | Btu/hr | 18 | SEER | 12.5 | EER | [7 empty] | Electric | N/A
17- 584823-1 | Electric Zonal | CUH-1-02 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | Wall Mounted Cabinet Unit Heater
17- 584823-1 | Electric Zonal | CUH-2-01 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Wall Mounted Cabinet Unit Heater
17- 584823-1 | Electric Zonal | CUH-2-02 | [6 empty] | 2.5 | kW |  |  |  |  | Electric |  | N/A |  | Wall Mounted Cabinet Unit Heater
17- 584823-1 | Electric Zonal | UH-G-01 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | Cabinet Unit Heater
17- 584823-1 | Electric Zonal | UH-G-02 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Cabinet Unit Heater
17- 607886-1 | Gas Zonal | UH-1 | [6 empty] | 75 | MBH | 80 | % |  |  | Natural Gas |  | N/A
17- 607886-1 | Ductless Heat Pump | CU-1 | Unknown |  | 9.4 | EER | 18 | SEER | Unknown |  | 9 | HSPF |  |  | Electric | Electric | No |  | No capacities listed
17- 634478-1 | Gas Heat/Direct Expansion Rooftop HVAC | GP-1 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A
17- 634478-1 | Electric Zonal | UH-1 | [6 empty] | 7500 | Watts |  |  |  |  | Electric |  | N/A
17- 636076-1 | Ductless Heat Pump | HCU-1 | 10.9 | MBH | 20 | SEER |  |  | 13.3 | MBH | 12 | HSPF |  |  | Electric | Electric | No |  | Daikin FTX12NMVJU; wall mounted
17- 636076-1 | Ductless Air Conditioner | CU-1 | 48 | MBH | 18.8 | SEER | 10.3 | EER | [7 empty] | Electric | N/A |  | Daikin RMXS48LVJU; serves several rooms; wall mounted
17- 636076-1 | Ductless Air Conditioner | CU-2 | 36 | MBH | 17.7 | SEER | 9.7 | EER | [7 empty] | Electric | N/A |  | Daikin RMXS36LVJU; serves several rooms; wall mounted
17- 636076-1 | Ductless Air Conditioner | CU-5 | 18 | MBH | 18.9 | SEER | 12.5 | EER | [7 empty] | Electric | N/A |  | Daikin RMXS18LVJU; serves several rooms; wall mounted
17- 636076-1 | Packaged Terminal Heat Pump | VTHP-1 | 9 | MBH | 10.5 | EER |  |  | 8.5 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 2.5 kW | Friedrich VHA09K
17- 636076-1 | Packaged Terminal Heat Pump | VTHP-2 | 12 | MBH | 10.3 | EER |  |  | 11.5 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 2.5 kW | Friedrich VHA12K
17- 636076-1 | Packaged Terminal Heat Pump | VTHP-3 | 17 | MBH | 9.1 | EER |  |  | 16 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 2.5 kW | Friedrich VHA18K
17- 636076-1 | Packaged Terminal Heat Pump | VTHP-4 | 23 | MBH | 9.1 | EER |  |  | 20 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 3.4 kW | Friedrich VHA24K
17- 636076-1 | Electric Zonal | EH-1 | [6 empty] | 0.5 | kW |  |  |  |  | Electric |  | N/A |  | Markel F30522TDWB; electric heater
17- 636076-1 | Electric Zonal | EH-3 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Markel F30522TDWB; electric heater
17- 636076-1 | Electric Zonal | EH-4 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Markel HF3326TD-RP; electric heater
17- 637259-1 | Gas Heat/Direct Expansion Rooftop HVAC | FCU05000 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Furnace
17- 642436-1 | Electric Zonal | EH-1 | [6 empty] | 1200 | Watts |  |  |  |  | Electric |  | N/A |  | Electric wall heater
17- 642436-1 | Packaged Terminal Heat Pump | HP-51 | 5175 | Btu/hr | 11.6 | EER |  |  | 4800 | Btu/hr | 3.6 | COP(47) |  |  | Electric | Electric | Yes | 2 kW
17- 642436-1 | Packaged Terminal Heat Pump | HP-82 | 5335 | Btu/hr | 11.5 | EER |  |  | 6000 | Btu/hr | 3.6 | COP(47) |  |  | Electric | Electric | Yes | 2 kW
16- 505459-1 | Ductless Air Conditioner | FC-3 , CU-3 | 6.95 | MBH | 15 | SEER | [9 empty] | Electric | N/A
16- 505459-1 | Ductless Air Conditioner | FC-4 , CU-4 | 14.46 | MBH | 15 | SEER | [9 empty] | Electric | N/A
16- 505459-1 | Electric Zonal | EH-8 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
16- 505459-1 | Electric Zonal | EH-9 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
17- 676005-1 | Air Source Heat Pump (Split System) | FC-2, CU-2 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | There is split system AC unit schedule in both electric and gas
17- 676005-1 | Electric Zonal | EH-3 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | Serves shower 106
17- 676005-1 | Electric Zonal | UH-3 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Bike storage 103
16- 507255-1 [Corridors] | Air Source Heat Pump (Split System) | HP-3 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Carrier 38MAQB12; serves electrical room; heating: 12000 BTUH 10 HSPF; cooling: 12000 BTUH 21.5 SEER
16- 507255-1 [Corridors] | Ductless Air Conditioner | OAC-1 | 30000 | Btu/hr | 15 | SEER | [9 empty] | Electric | N/A |  | Carrier 24ACC630
16- 507255-1 [Corridors] | Ductless Air Conditioner | OAC-3 | 41500 | Btu/hr | 15 | SEER | [9 empty] | Electric | N/A |  | Carrier 24ACC642
16- 507255-1 [Corridors] | Ductless Heat Pump | VTAC-3 | 8800 | Btu/hr | 10.5 | EER |  |  | 8200 | Btu/hr | 3.4 | COP(47) |  |  | Electric | Electric | Yes | 4.07 kW | GE AZ85H09EAC
17- 697310-1 | Electric Zonal | ERV-B2-2 | [6 empty] | 5.5 | kW |  |  |  |  | Electric |  | N/A |  | Electric Duct Heater
17- 697310-1 | Electric Zonal | EH-3 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater
17- 697310-1 | Electric Zonal | EH-4 | [6 empty] | 4.8 | kW |  |  |  |  | Electric |  | N/A |  | Electric Unit Heater
17- 719811-1 | Other Rooftop HVAC | PACU-1 | 122 | MBH | Unknown |  |  |  | 117 | MBH | Unknown | Unknown |  |  | Electric | Electric | N/A |  | This is a pool air conditioning unit
17- 719811-1 | Electric Zonal | EUH-1 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
17- 719811-1 | Electric Zonal | EUH-4 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
17- 719811-1 | Electric Zonal | EWH-1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
17- 719811-1 | Packaged Terminal Heat Pump | VTAC 1 | 12 | MBH | 13 | EER |  |  | 11.5 | MBH | 3.4 | COP(47) |  |  | Electric | Electric | Yes | 3.4 kW | This is the "alternate bid" schedule
17- 719811-1 | Packaged Terminal Heat Pump | VTAC 2 | 23.4 | MBH | 11 | EER |  |  | 21 | MBH | 3.1 | COP(47) |  |  | Electric | Electric | Yes | 3.4 kW | This is the "alternate bid" schedule
17- 719811-1 | Ductless Air Conditioner | RACU-9 | 36 | MBH | 14 | SEER | [9 empty] | Electric | N/A |  | serves PBX
17- 719811-1 | Ductless Air Conditioner | RACU-8 | 18 | MBH | 15.3 | SEER | [9 empty] | Electric | N/A |  | Electrical
16- 640577-1 | Packaged Terminal Heat Pump | PTAC-1 | 7.1 | MBH | Unknown |  |  |  | 8.2 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3.3 kW | Schedule is difficult to read. No efficiencies included. GE AZ…
16- 640577-1 | Packaged Terminal Heat Pump | PTAC-2 | 8.2 | MBH | Unknown |  |  |  | 8.5 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 8.2 kW | Schedule is difficult to read. No efficiencies included. GE AZ…
16- 640577-1 | Ductless Air Conditioner | AC-2 | 8000 | Btu/hr | [11 empty] | Electric | N/A |  | No efficiency given; Schedule is difficult to read
16- 640577-1 | Electric Zonal | UH-5 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Maywell AFC; serves Vestrule 1
16- 640577-1 | Electric Zonal | UH-7 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Maywell S100
16- 640577-1 | Electric Zonal | UH-9 | [6 empty] | 8 | kW |  |  |  |  | Electric |  | N/A |  | Maywell S100
17- 777891-1 [Common area] | Ductless Air Conditioner | ACU-1 | 12 | MBH | 15.2 | SEER | [9 empty] | Electric | N/A
17- 777891-1 [Common area] | Electric Zonal | AEH-1 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A
17- 792314-1 | Electric Zonal | BB-2 | [6 empty] | 0.75 | kW |  |  |  |  | Electric |  | N/A |  | Markel F3707-040B; serves vestibule
17- 792314-1 | Electric Zonal | UH-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Qmark MUH05-81; serves mechanical room
17- 803573-1 [Misc.] | Ductless Heat Pump | OHP-1 | 60 | MBH | 17 | SEER |  |  | 60 | MBH | 10.7 | HSPF |  |  | Electric | Electric | No |  | Mitsubishi PUMY-P60NKMU-1; serves lobby/hall; outdoor heat pump, separate from 1-1 heat pumps (ASHP AHU/ASHP RTU)
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-A | 32000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXT; serves two IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-B | 21000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXT; serves three IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-D | 28000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXT; serves four IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-E1 | 23000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXT; serves three IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-E2 | 50000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXTQ; serves two IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-E3 | 30000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXTQ; serves four IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-F | 14000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXT; serves two IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-F300 | 9000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin FTX; serves one IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-F307 | 7000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin FTX; serves one IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-H | 36000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXT; serves two IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | OAC-S201 | 24000 | Btu/hr | 18 | SEER | [9 empty] | Electric | N/A |  | Daikin RXS24LVJU; serves one IACs
16- 735523-1 [Classrooms, commons, misc.] | Ductless Air Conditioner | CU-1 | 785.5 | MBH | 10.6 | EER | [9 empty] | Electric | N/A |  | Daikin RCS-072D
17- 813087-1 | Ductless Air Conditioner | CU-1 | 12 | MBH | 15 | SEER | [9 empty] | Electric | N/A |  | serves elevator equipment room
17- 813087-1 | Electric Zonal | EH-3 | [6 empty] | 1.125 | kW |  |  |  |  | Electric |  | N/A
17- 813087-1 | Electric Zonal | EH-6 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
17- 815466-1 | Electric Zonal | EH-1 | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A |  | Qmark GFR2004F; electric wall heater
17- 815466-1 | Electric Zonal | EH-2 | [6 empty] | 1125 | Watts |  |  |  |  | Electric |  | N/A |  | Qmark GFR2004F; electric wall heater
17- 815466-1 | Electric Zonal | UH-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Modine HER50B3101; electric unit heater
17- 815466-1 | Electric Zonal | UH-2 | [6 empty] | 7.5 | kW |  |  |  |  | Electric |  | N/A |  | Modine HER75B3101; electric unit heater
17- 821806-1 | Ductless Heat Pump | HP-1 | 12 | MBH | 23 | SEER |  |  | 14 | MBH |  |  |  |  | Electric | Electric | No |  | Carrier RAS-12EKV-UL; No heating efficiency given
17- 830379-1 | Gas Zonal | UH-3 | [6 empty] | 30 | MBH | 82 | % |  |  | Natural Gas |  | N/A
17- 830379-1 | Gas Zonal | IR-2 | [6 empty] | 65 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | According to the comcheck files, no minimum efficiency requirement applies for this radiant heater
17- 830379-1 | Ductless Heat Pump | HP-8 | 8 | MBH | 15 | SEER |  |  | 11 | MBH | 9.6 | HSPF |  |  | Electric | Electric | No
17- 830379-1 | Ductless Air Conditioner | AC-1 | 18 | MBH | 15.3 | SEER | [9 empty] | Electric | N/A
17- 832860-1 [Living area] | Ductless Air Conditioner | ACCU-1 | 21.2 | MBH | 18 | SEER | [9 empty] | Electric | N/A
17- 855496-1 [Living] | Gas Zonal | GUH | [6 empty] | 300 | MBH | 83 | % |  |  | Natural Gas |  | N/A
17- 855496-1 [Living] | Electric Zonal | EUH-4 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
17- 855496-1 [Living] | Electric Zonal | EUH-6 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
17- 855496-1 [Living] | Electric Zonal | EUH-7 | [6 empty] | 3.3 | kW |  |  |  |  | Electric |  | N/A
17- 855496-1 [Living] | Gas Zonal | GRH-4 | [6 empty] | 60000 | Btu/hr | Unknown |  |  |  | Natural Gas |  | N/A
17- 855496-1 [Living] | Ductless Air Conditioner | CU-1 | 22.2 | MBH | 15.9 | SEER | [9 empty] | Electric | N/A
17- 855496-1 [Living] | Ductless Heat Pump | HP-5 | 9.1 | MBH | 18 | SEER |  |  | 10 | MBH |  |  |  |  | Electric | Electric | Unknown
17- 855496-1 [Living] | Ductless Heat Pump | HP-7 | 24 | MBH | 18 | SEER |  |  | 24 | MBH |  |  |  |  | Electric | Electric | Unknown
17- 856087-1 | Electric Zonal | EWH-3 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | Electric Wall Heater; Manager room
17- 856087-1 | Electric Zonal | EDH-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Electric Duct Heater; ERV supply
17- 866279-1 | Electric Zonal | UH-01 | [6 empty] | 1.8 | kW |  |  |  |  | Electric |  | N/A |  | Qmark EFQ60D6; serves production distillery
18- 576787-1 | Electric Zonal | DH-1 | [6 empty] | 8 | kW |  |  |  |  | Electric |  | N/A
18- 576787-1 | Electric Zonal | EWH | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A
18- 576787-1 | Electric Zonal | RCP | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A
18- 576787-1 | Other Rooftop HVAC | IH-4 | Unknown | [5 empty] | 80 | MBH | Unknown | Unknown |  |  | Propane |  | N/A |  | Heating fuel type: Propane
18- 585712-1 | Electric Zonal | EWH-2 | [6 empty] | 4800 | Watts |  |  |  |  | Electric |  | N/A |  | Wall heater; Berko SSARWH4808
18- 585712-1 | Electric Zonal | EWH-11 | [6 empty] | 8000 | Watts |  |  |  |  | Electric |  | N/A |  | Wall heater; Berko EFQ80048
18- 585712-1 | Electric Zonal | EWH-13 | [6 empty] | 1800 | Watts |  |  |  |  | Electric |  | N/A |  | Wall heater; Berko SSARWH1802
18- 585712-1 | Electric Zonal | UH-2 | [6 empty] | 15000 | Watts |  |  |  |  | Electric |  | N/A |  | Unit heater; Reznor EWHB-15
18- 585712-1 | Electric Zonal | UH-9 | [6 empty] | 30000 | Watts |  |  |  |  | Electric |  | N/A |  | Unit heater; Reznor EWHB-30
18- 585712-1 | Electric Zonal | UH-10 | [6 empty] | 10000 | Watts |  |  |  |  | Electric |  | N/A |  | Unit heater; Reznor EWHB-10
18- 585712-1 | Electric Zonal | EB-3 | [6 empty] | 3750 | Watts |  |  |  |  | Electric |  | N/A |  | Baseboard heater; QMARK CPH07A5750
18- 585712-1 | Electric Zonal | EB-6 | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A |  | Baseboard heater; QMARK CPH05A3250
18- 585712-1 | Electric Zonal | RM-11 | [6 empty] | Unknown | [5 empty] | Electric |  | N/A |  | In-floor radiant heater; Watts 1"M Series; 1771 SQ-FT, 28.2 MBH heating output
18- 585712-1 | Electric Zonal | DH-3 | [6 empty] | 20 | kW |  |  |  |  | Electric |  | N/A |  | Duct mounted electrical heater; Renewaire EK
18- 612115-1 | Electric Zonal | UH-5 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Qmark IUH-520; 6 HP fan; serves storage 205
18- 612115-1 | Electric Zonal | UH-6 | [6 empty] | 15 | kW |  |  |  |  | Electric |  | N/A |  | Qmark IUH-1524; 0.1 HP fan; serves storage building
18- 612115-1 | Electric Zonal | EWH-2 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Qmark AWH wall mounted; serves equipment platform 204
18- 625157-1 | Air Source Heat Pump (Packaged) | HP-6 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Cooling 19.2 MBH, EER of 12, SEER 14, 800 CFM, Heating 22 MBH, 2 kW
18- 641081-1 | Electric Zonal | CDBC-UH-01 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | King KBP2006-3MP; serves water service room
18- 641081-1 | Electric Zonal | CDBC-UH-03 | [6 empty] | 10 | kW |  |  |  |  | Electric |  | N/A |  | Indeeco UHIR; serves loading dock
18- 641081-1 | Electric Zonal | CDBC-UH-04 | [6 empty] | Unknown | kW |  |  |  |  | Electric |  | N/A |  | King PAW-1215; serves toilet 134
18- 641081-1 | Electric Zonal | CDBC-UH-05 | [6 empty] | 0.5 | kW |  |  |  |  | Electric |  | N/A |  | King PAW-1215; serves storage
18- 641081-1 | Electric Zonal | CDBC-UH-AR | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | King KB4810-3MP; serves quad 2 pump room
18- 650512-1 | Electric Zonal | UH-105 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | Wall recessed; Q-Mark AWH
18- 650512-1 | Electric Zonal | UH-107 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | Meter & Disconnect; Q-Mark CWH
18- 650512-1 | Electric Zonal | UH-108 | [6 empty] | 4.8 | kW |  |  |  |  | Electric |  | N/A |  | Wall recessed; Q-Mark AWH
18- 650512-1 | Electric Zonal | UH-111 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Ceiling mount infrared; Q-Mark HRK
18- 650512-1 | Electric Zonal | UH-402 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Surface mount; Q-Mark AWH
18- 596289-1 | Gas Zonal | UH-1 | [6 empty] | 120000 | Btu/hr | 83 | % |  |  | Natural Gas |  | N/A |  | Reznor UDAP125 V3 series; 1/4 motor HP; gas fired unit heater
18- 596289-1 | Ductless Air Conditioner | AC-1/CU-1 | 1.5 | Tons | 18.6 | SEER | [9 empty] | Electric | N/A |  | Daikin FAQ18PVJU/Daikin RZR18PVJU; serves TDP165
18- 596289-1 | Electric Zonal | EUH 6 | [6 empty] | 10 | kW |  |  |  |  | Electric |  | N/A |  | Qmark MUH; 34.1 MBH total capacity; 0.03 HP 650 cfm fan; electric unit heater
18- 704117-1 | Gas Heat/Direct Expansion Rooftop HVAC | CU-1 | 168000 | Btu/hr | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | 168,000 btu/h rooftop condensing unit to cool electrical rooms
18- 704117-1 | Electric Zonal | EUH-1-2 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A
18- 704117-1 | Electric Zonal | EUH-R-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
18- 723839-1 | Packaged Terminal Heat Pump | VTAC-1 | 12000 | Btu/hr | 13 | EER |  |  | 11500 | Btu/hr | 3.4 | COP(47) |  |  | Electric | Electric | Yes | 2.78 | Friedrich VPH12
18- 723839-1 | Electric Zonal | EWH-6 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | BROAN 198; wall mounted
18- 723839-1 | Ductless Air Conditioner | OAC-1 | 22000 | Btu/hr | 21 | SEER | [9 empty] | Electric | N/A |  | LG LSU240HLV; Elevator equipment room
18- 737861-1 | Packaged Terminal Heat Pump | PTAC-1 | 7.1 | MBH | Unknown |  |  |  | 6.2 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3.2 kW
18- 737861-1 | Packaged Terminal Heat Pump | PTAC-2 | 9.2 | MBH | Unknown |  |  |  | 8.1 | MBH | Unknown |  |  |  | Electric | Electric | Yes | 3.2 kW
18- 737861-1 | Ductless Air Conditioner | AC-2 | 9000 | Btu/hr | Unknown | [10 empty] | Electric | N/A
18- 737861-1 | Air Source Heat Pump (Packaged) | VTAC-3 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | GE
18- 737861-1 | Electric Zonal | UH-5 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | No cooling
18- 737861-1 | Electric Zonal | UH-9 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | No cooling
18- 811956-1 | Gas Zonal | UH-1 | [6 empty] | 120 | MBH | 83 | % |  |  | Natural Gas |  | N/A |  | Reznor UDAP-125
18- 811956-1 | Electric Zonal | DH-1 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | Markel 1201HF1KW8W8H241HRGH1; electric duct heater
18- 811956-1 | Electric Zonal | WH-5 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A |  | Broan 170; electric wall heater
18- 863748-1 | Ductless Air Conditioner | ID-02 | 24 | MBH | Unknown | [10 empty] | Electric | N/A |  | Cooling Only, total cooling capacity, no efficiency listed
18- 863748-1 | Ductless Air Conditioner | ID-03 | 6 | MBH | Unknown | [10 empty] | Electric | N/A |  | Cooling Only, total cooling capacity, no efficiency listed
18- 863748-1 | Ductless Air Conditioner | ID-04 | 15 | MBH | Unknown | [10 empty] | Electric | N/A |  | Cooling Only, total cooling capacity, no efficiency listed
18- 863748-1 | Ductless Air Conditioner | AC-01 | 60 | MBH | 18.6 | SEER | [9 empty] | Electric | N/A |  | Cooling Only, total cooling capacity
18- 899620-1 | Electric Zonal | EH-1.1 | [6 empty] | 375 | Watts |  |  |  |  | Electric |  | N/A
18- 899620-1 | Electric Zonal | EH-4.1 | [6 empty] | 2000 | Watts |  |  |  |  | Electric |  | N/A
18- 899620-1 | Electric Zonal | RH-3.34 | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A
19- 700419-1 | Gas Zonal | UH-4 | [6 empty] | 100000 | Btu/hr | 80 | % |  |  | Natural Gas |  | N/A |  | Modine HD100; serves receiving
19- 700419-1 | Gas Heat/Direct Expansion Rooftop HVAC | F-1 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Furnace with condensing unit; Trane TDH1C0859H4; serves entry/exit 168
19- 700419-1 | Ductless Heat Pump | CU-1 | 22200 | Btu/hr | 15 | SEER |  |  | 24200 | Btu/hr | 8 | HSPF |  |  | Electric | Electric | No |  | Fujitsu AOU24RLX outdoor unit; ductless ceiling cassette; serves MDF room
19- 700419-1 | Ductless Heat Pump | CU-3 | 9000 | Btu/hr | 24 | SEER |  |  | 12000 | Btu/hr | 13 | HSPF |  |  | Electric | Electric | No |  | Fujitsu AOU9RLFC outdoor unit; ductless wall mount; serves ICC office
19- 700419-1 | Ductless Heat Pump | CU-6 | 22000 | Btu/hr | 18 | SEER |  |  | 27600 | Btu/hr | 10 | HSPF |  |  | Electric | Electric | No |  | Fujitsu AOU24RLXFW outdoor unit; ductless wall mount; serves concierge
19- 700419-1 | Packaged Terminal Heat Pump | CU-5 | 18000 | Btu/hr | 19.7 | SEER |  |  | 21600 | Btu/hr | 11.3 | HSPF |  |  | Electric | Electric | No |  | Fujitsu AOU18RLFC outdoor unit; ducted; serves Vendor, customer service
19- 730078-1 | Ductless Heat Pump | MSU-1.3 | 34 | MBH | 8.18 | EER | 17.5 | SEER | 38 | MBH | 10.1 | HSPF |  |  | Electric | Electric | Unknown |  | LG LS363HLV; serves mechanical room
19- 730078-1 | Ductless Heat Pump | MSU-1.5 | 30 | MBH | 10 | EER | 19 | SEER | 32 | MBH | 10 | HSPF |  |  | Electric | Electric | Unknown |  | LG LS303HLV; serves office
19- 730078-1 | Other Rooftop HVAC | HUH-1.2 | Unknown | [5 empty] | 58.4 | MBH | Unknown |  |  |  | Electric |  | N/A |  | Zehnder-Rittling RH-108
19- 730078-1 | Electric Zonal | EUH-1.3 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Electric unit heater; Markel 5100 Series
19- 731945-1 | Ductless Air Conditioner | CU-3 | 9000 | Btu/hr | 19 | SEER | [9 empty] | Electric | N/A |  | Daikin RK09NMVJU
19- 731945-1 | Ductless Air Conditioner | CU-5 | 22890 | Btu/hr | 17.9 | SEER | [9 empty] | Electric | N/A |  | Daikin RKS36LVJU
19- 731945-1 | Electric Zonal | EWH-1 | [6 empty] | 1500 | Watts |  |  |  |  | Electric |  | N/A |  | Wall heater; Trane UHAA
19- 731945-1 | Electric Zonal | UH-1 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | Unit heater; Trane UHEC 053 DA
19- 731945-1 | Electric Zonal | R-1 | [6 empty] | 879 | Watts |  |  |  |  | Electric |  | N/A |  | Electric baseboard radiators; Runtal PED-208D
19- 731945-1 | Electric Zonal | R-2 | [6 empty] | 1025 | Watts |  |  |  |  | Electric |  | N/A |  | Electric baseboard radiators; Runtal PED-208D
19- 731945-1 | Electric Zonal | R-3 | [6 empty] | 1172 | Watts |  |  |  |  | Electric |  | N/A |  | Electric baseboard radiators; Runtal PED-208D
19- 731945-1 | Electric Zonal | R-4 | [6 empty] | 1319 | Watts |  |  |  |  | Electric |  | N/A |  | Electric baseboard radiators; Runtal PED-208D
19- 731945-1 | Electric Zonal | R-5 | [6 empty] | 1466 | Watts |  |  |  |  | Electric |  | N/A |  | Electric baseboard radiators; Runtal PED-208D
18- 596300-1 | Gas Zonal | UH-3 | [6 empty] | 145000 | Btu/hr | 80 | % |  |  | Natural Gas |  | N/A |  | Lennox LF24-145A; 1/8 HP fan; serves staging area
19- 765123-1 | Ductless Heat Pump | HP-2 | 30000 | Btu/hr | 12 | EER | 14.5 | SEER | 30000 | Btu/hr | 2.7 | COP(47) |  |  | Electric | Electric | No |  | Trane 4TWR4030G
19- 765123-1 | Ductless Heat Pump | HP-3 | 36000 | Btu/hr | 12.5 | EER | 18 | SEER | 36000 | Btu/hr | 3.2 | COP(47) |  |  | Electric | Electric | No |  | Trane 4TWV8036A
98- 927699-1 | Electric Zonal | DH-1 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
98- 927699-1 | Electric Zonal | DH-3 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A
98- 927699-1 | Electric Zonal | DH-4 | [6 empty] | 5.5 | kW |  |  |  |  | Electric |  | N/A
98- 927699-1 | Electric Zonal | DH-5 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
98- 927699-1 | Gas Heat/Direct Expansion Rooftop HVAC | RTU-2 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A
98- 927699-1 | Ductless Air Conditioner | CU-3 | 12 | MBH | 20.5 | SEER | [9 empty] | Electric | N/A
98- 927699-1 | Ductless Air Conditioner | CU-4 | 45 | MBH | 20.5 | SEER | [9 empty] | Electric | N/A
15- 689971-1 | Ductless Air Conditioner | CU-2 | 24 | MBH | 15 | SEER | [9 empty] | Electric | N/A |  | No notes on area served
15- 689971-1 | Ductless Air Conditioner | CU-4 | 18 | MBH | 15 | SEER | [9 empty] | Electric | N/A |  | No notes on area served
15- 689971-1 | Electric Zonal | EH-15 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A |  | Surface mount
15- 689971-1 | Electric Zonal | EH-20 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Surface mount
15- 689971-1 | Electric Zonal | EH-21 | [6 empty] | 2.25 | kW |  |  |  |  | Electric |  | N/A |  | Surface mount
19- 506267-1 | Ductless Heat Pump | HP-8 | 36 | MBH | 19.1 | SEER |  |  | 45 | MBH | 11.3 | HSPF |  |  | Electric | Electric | Unknown |  | Mitsubishi MXZ-4C36NAHZ
19- 506267-1 | Ductless Air Conditioner | CU-9 | 24 | MBH | 21.4 | SEER | [9 empty] | Electric | N/A |  | Mitsubishi PUY-A24NHA7; serves elevator machine room
19- 506267-1 | Packaged Terminal Heat Pump | PTHP-1 | 12 | MBH | 11.9 | EER |  |  | 8 | MBH | 3.5 | COP(47) |  |  | Electric | Electric | No |  | LG LP123HDUC1
19- 506267-1 | Packaged Terminal Heat Pump | PTHP-2 | 15 | MBH | 11.2 | EER |  |  | 8 | MBH | 3.1 | COP(47) |  |  | Electric | Electric | No |  | LG LP153HDUC
19- 506267-1 | Electric Zonal | EH-1 | [6 empty] | 0.5 | kW |  |  |  |  | Electric |  | N/A |  | Q-Mark CWH1101DSF
18- 625974-1 | Ductless Heat Pump | CCU-3 | 12000 | Btu/hr | 20.8 | SEER |  |  | 8000 | Btu/hr | Unknown |  |  |  | Electric | Electric | No |  | Mitsubishi MUZ-FH12NA
18- 625974-1 | Packaged Terminal Air Conditioner | PTAC | 7.1 | MBH |  |  | 13 | EER | [6 empty] | Electric | Electric |  | Yes | Auxiliary electric heat 8.2 MBH, 2.4 kW
16- 709134-1 | Electric Zonal | EH-2 | [6 empty] | 8 | kW |  |  |  |  | Electric |  | N/A
16- 709134-1 | Ductless Heat Pump | AC-1 | 24000 | Btu/hr | 19.5 | SEER |  |  | 24000 | Btu/hr |  |  |  |  | Electric | Electric | No
16- 709134-1 | Ductless Heat Pump | AC-2 | 36000 | Btu/hr | 19.5 | SEER |  |  | 36000 | Btu/hr |  |  |  |  | Electric | Electric | No
18- 554364-1 [Administrative] | Ductless Air Conditioner | CU-201 | 24 | MBH | 17 | SEER | [9 empty] | Electric | N/A
18- 554364-1 [Administrative] | Electric Zonal | EH-101 | [6 empty] | 4.8 | kW |  |  |  |  | Electric |  | N/A
18- 554364-1 [Administrative] | Electric Zonal | EH-103 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
18- 554364-1 [Administrative] | Electric Zonal | EH-104 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
18- 554364-1 [Administrative] | Electric Zonal | EH-106 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
08- 723130-1 | Electric Zonal | RCP | [6 empty] | 750 | Watts |  |  |  |  | Electric |  | N/A |  | Radiant Ceiling Panel, no cooling
08- 723130-1 | Electric Zonal | EIH | [6 empty] | 2000 | Watts |  |  |  |  | Electric |  | N/A |  | Electric Infrared Heater, no cooling
08- 723130-1 | Gas Zonal | IH-3 | [6 empty] | 115 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | Infrared Tube Heater, no cooling, no output, no efficiencies listed
08- 723130-1 | Electric Zonal | DH-1 | [6 empty] | 12 | kW |  |  |  |  | Electric |  | N/A |  | Electric Duct Heater, no cooling
08- 723130-1 | Electric Zonal | DH-2 | [6 empty] | 15 | kW |  |  |  |  | Electric |  | N/A |  | Electric Duct Heater, no cooling
08- 723130-1 | Electric Zonal | EWH-1 | [6 empty] | 1000 | Watts |  |  |  |  | Electric |  | N/A |  | Electric Wall Heater, no cooling
12- 456419-1 | Ductless Air Conditioner | CU-101 | 17.8 | MBH | 13 | SEER | [9 empty] | Electric | N/A |  | No heating; Unknown service area
12- 456419-1 | Electric Zonal | EH-2 | [6 empty] | 2.3 | kW |  |  |  |  | Electric |  | N/A
12- 456419-1 | Electric Zonal | EH-3 | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
12- 456419-1 | Electric Zonal | EH-5 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A
12- 456419-1 | Electric Zonal | UH-1 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A
12- 456419-1 | Electric Zonal | UH-3 | [6 empty] | 7.5 | kW |  |  |  |  | Electric |  | N/A
18- 614250-1 | Other Rooftop HVAC | AHU-R1 | 253.1 | MBH | 11.1 | EER |  |  | 156.8 | MBH | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Hot water pre-heat coil (heating)
18- 614250-1 | Other Rooftop HVAC | AHU-R2 | 187.2 | MBH | 10.9 | EER |  |  | 125.4 | MBH | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Hot water pre-heat coil (heating)
18- 614250-1 | Ductless Air Conditioner | IAC/OAC-01 | 4 | Tons | 17 | SEER | [9 empty] | Electric | N/A
18- 614250-1 | Ductless Air Conditioner | IAC/OAC-02 | 1 | Tons | 22.7 | SEER | [9 empty] | Electric | N/A
18- 535655-1 | Electric Zonal | WH#1 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Markel HF3324TTD-RP; serves drive thru
13- 658146-1 [Other] | Electric Zonal | EUH-2 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
13- 658146-1 [Other] | Electric Zonal | EUH-4 | [6 empty] | Unknown | kW |  |  |  |  | Electric |  | N/A |  | Capacity is 0.25 KW
13- 658146-1 [Other] | Electric Zonal | SFPB 1.1 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A |  | CFM of 940
13- 658146-1 [Other] | Electric Zonal | SFPB 1.2 | [6 empty] | 10 | kW |  |  |  |  | Electric |  | N/A |  | CFM of 1980
13- 658146-1 [Other] | Electric Zonal | SFPB 1.3 | [6 empty] | 6 | kW |  |  |  |  | Electric |  | N/A |  | Electric Heater CFM of 1020
13- 658146-1 [Other] | Electric Zonal | SFPB 1.4 | [6 empty] | 0.5 | kW |  |  |  |  | Electric |  | N/A |  | Electric Heater CFM of 200
13- 658146-1 [Other] | Electric Zonal | SFPB 2.4 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | Electric Heater CFM of 200
13- 658146-1 [Other] | Electric Zonal | SFPB 2.7 | [6 empty] | 9 | kW |  |  |  |  | Electric |  | N/A |  | Electric Heater CFM of 2200
13- 658146-1 [Other] | Ductless Air Conditioner | FCU 1.2 | 18.5 | MBH | 12.2 | EER | 21.4 | SEER | [7 empty] | Electric | N/A |  | Air Conditioning Unit Schedule with split system AC fan coils
19- 820425-1 | Packaged Terminal Heat Pump | PTAC-1 | 9400 | Btu/hr | 12.1 | EER |  |  | 8500 | Btu/hr | 3.51 | COP(47) |  |  | Electric | Electric | No | N/A
19- 820425-1 | Ductless Air Conditioner | OAC-1 | 22000 | Btu/hr | 21 | SEER | [9 empty] | Electric | N/A |  | elevator equipment room
19- 820425-1 | Electric Zonal | WH-1 (5) | [6 empty] | 3 | kW |  |  |  |  | Electric |  | N/A
17- 799406-1 | Ductless Air Conditioner | CU-5 | 27.3 | MBH | Unknown | [10 empty] | Electric | N/A |  | no efficiency included
17- 799406-1 | Ductless Heat Pump | CU-2 | 29.5 | MBH | Unknown |  |  |  | 9.6 | MBH | Unknown |  |  |  | Electric | Electric | No | N/A | No efficiency included
17- 799406-1 | Ductless Heat Pump | CU-3 | 38.1 | MBH | Unknown |  |  |  | 9.4 | MBH | Unknown |  |  |  | Electric | Electric | No | N/A | No efficiency included
17- 799406-1 | Ductless Heat Pump | CU-6 | 32.1 | MBH | Unknown |  |  |  | 11.3 | MBH | Unknown |  |  |  | Electric | Electric | No | N/A | No efficiency included
17- 799406-1 | Ductless Heat Pump | CU-7 | 11.9 | MBH | Unknown |  |  |  | 11.5 | MBH | Unknown |  |  |  | Electric | Electric | No | N/A | No efficiency included
17- 799406-1 | Ductless Heat Pump | CU-8 | 17.7 | MBH | Unknown |  |  |  | 11.5 | MBH | Unknown |  |  |  | Electric | Electric | No | N/A | No efficiency included
17- 799406-1 | Electric Zonal | EUH-3 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A
17- 799406-1 | Gas Zonal | GUH-3 | [6 empty] | 240 | MBH | 80 | % |  |  | Natural Gas |  | N/A |  | heat only
17- 551538-3 | Electric Zonal | EWH-1 | [6 empty] | 1125 | Watts |  |  |  |  | Electric |  | N/A
17- 551538-3 | Electric Zonal | EWH-2 | [6 empty] | 7500 | Watts |  |  |  |  | Electric |  | N/A
17- 551538-3 | Electric Zonal | EWH-3 | [6 empty] | 9900 | Watts |  |  |  |  | Electric |  | N/A
17- 701880-1 | Gas Heat/Direct Expansion Rooftop HVAC | RTU-01 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Natural Gas | Electric | N/A |  | Daikin DPS005A
17- 701880-1 | Gas Zonal | GUH-03 | [6 empty] | 150 | MBH | Unknown |  |  |  | Natural Gas |  | N/A |  | Low fire capacity of 115 MBH; DUH-150
17- 701880-1 | Electric Zonal | EUH-05 | [6 empty] | 1.5 | kW |  |  |  |  | Electric |  | N/A |  | Marley CWH1202DSAF
14- 689118-1 | Ductless Heat Pump | DS-4a | 22 | MBH | 15 | SEER | 9.2 | EER | 22 | MBH | Unknown |  |  |  | Electric | Electric | No |  | Daikin RXN24NMVJU
14- 689118-1 | Ductless Heat Pump | DS-5a | 36 | MBH | 15.9 | SEER |  |  | 36 | MBH | 2.78 | COP(47) |  |  | Electric | Electric | No |  | Daikin RX36NMVJU
14- 689118-1 | Packaged Terminal Heat Pump | VTHP-A | 9 | MBH | 10.5 | EER |  |  | 8.5 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 2.5 kW | Friedrich VHA09K
14- 689118-1 | Packaged Terminal Heat Pump | VTHP-B | 12 | MBH | 10.5 | EER |  |  | 11.5 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 3.5 kW | Friedrich VHA12K
14- 689118-1 | Packaged Terminal Heat Pump | VTHP-C | 17 | MBH | 10.5 | EER |  |  | 16 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 5 kW | Friedrich VHA18K
14- 689118-1 | Packaged Terminal Heat Pump | VTHP-D | 23 | MBH | 10.5 | EER |  |  | 20 | MBH | 3 | COP(47) |  |  | Electric | Electric | Yes | 7.5 kW | Friedrich VHA24K
14- 689118-1 | Air Source Heat Pump (Split System) | HP-23 | Unknown |  | Unknown |  |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Carrier 25HCE460A0031
14- 689118-1 | Electric Zonal | FWH-7 | [6 empty] | 2 | kW |  |  |  |  | Electric |  | N/A |  | KING PAW2720
14- 689118-1 | Electric Zonal | EDH-14 | [6 empty] | 1 | kW |  |  |  |  | Electric |  | N/A |  | HOTPOD HP6-1000120-2CT
14- 689118-1 | Electric Zonal | EDH-13 | [6 empty] | 1.4 | kW |  |  |  |  | Electric |  | N/A |  | HOTPOD HP8-1000120-2CT
14- 689118-1 | Electric Zonal | EDH-15 | [6 empty] | 8 | kW |  |  |  |  | Electric |  | N/A |  | NAILOR DHRS W15 H14 HL 4803 STG 3S1 A1 24V P1N0 C4 T1 F1 D1 DL10 JA4
14- 689118-1 | Electric Zonal | EDH-16 | [6 empty] | 10 | kW |  |  |  |  | Electric |  | N/A |  | NAILOR DHRS W15 H14 HR 4803 STG 3S1 A1 24V P1N0 C4 T1 F1 D1 DL10 JA4
17- 550764-1 | Ductless Air Conditioner | ACCU-406 | 12 | MBH | 21.1 | SEER | 13 | EER | [7 empty] | Electric | N/A |  | Mitsubishi PKA/PUY; serves Elev Mech 136N
17- 550764-1 | Electric Zonal | ECUH-102 | [6 empty] | 4.8 | kW |  |  |  |  | Electric |  | N/A |  | TRANE UHAA; cabinet unit heater; serves 100 vestibule
17- 550764-1 | Electric Zonal | ECUH-103 | [6 empty] | 10 | kW |  |  |  |  | Electric |  | N/A |  | TRANE FORCE FLO; cabinet unit heater; serves 132 laundry
17- 550764-1 | Electric Zonal | ECUH-104 | [6 empty] | 4 | kW |  |  |  |  | Electric |  | N/A |  | TRANE UHAA; cabinet unit heater; serves M125N hall
17- 550764-1 | Electric Zonal | ECUH-202 | [6 empty] | 2.25 | kW |  |  |  |  | Electric |  | N/A |  | TRANE UHAA; cabinet unit heater; serves stair 3
17- 550764-1 | Electric Zonal | ECUH-203 | [6 empty] | 5 | kW |  |  |  |  | Electric |  | N/A |  | TRANE UHAA; cabinet unit heater; serves 200 vestibule
17- 550764-1 | Electric Zonal | CH-101 | [6 empty] | 500 | Watts |  |  |  |  | Electric |  | N/A |  | CADET COM-PAK; cadet heater; serves 145 janitor
17- 550764-1 | Electric Zonal | UH-106 | [6 empty] | 3.3 | kW |  |  |  |  | Electric |  | N/A |  | TRANE UHEC; unit heater; serves mech 131N
17- 550764-1 | Electric Zonal | EBH-001 | [6 empty] | 875 | Watts |  |  |  |  | Electric |  | N/A |  | INDEECO MINI; elec baseboard heater
17- 550764-1 | Electric Zonal | EBH-002 | [6 empty] | 1050 | Watts |  |  |  |  | Electric |  | N/A |  | INDEECO MINI; elec baseboard heater
15- 568036-2 | Ductless Heat Pump | HP-5 | 18000 | Btu/hr | 20.3 | SEER | 12.7 | EER | 21600 | Btu/hr | 3.7 | COP(47) | 11 | HSPF | Electric | Electric | No |  | Daikin RSX18LVJU
15- 568036-2 | Air Source Heat Pump (Split System) | HP-6 | Unknown |  | 10.5 | EER |  |  | Unknown |  | Unknown |  |  |  | Electric | Electric | Unknown |  | Carrier 25HCE436A003
15- 568036-2 | Ductless Heat Pump | HP-8 | 12000 | Btu/hr | 15 | SEER | 12.2 | EER | 12000 | Btu/hr | 3.9 | COP(47) | 8.2 | HSPF | Electric | Electric | No |  | Daikin RSN12NMVJU
15- 568036-2 | Ductless Heat Pump | HP-9 | 17100 | Btu/hr | 15 | SEER |  |  | 18000 | Btu/hr | 3.8 | COP(47) | 8.2 | HSPF | Electric | Electric | No |  | Daikin RSN18NMVJU
18- 559771-1 | Ductless Air Conditioner | DSS-2 | 12000 | Btu/hr | 20.8 | SEER | [9 empty] | Electric | N/A

## Stage2HRV
Project_ID | DOAS? | Equipment ID | Manufacturer | Model | OA Supply Airflow (CFM) | Exhaust Airflow (CFM) | Fan Power | Fan Power Units | Sensible Effectiveness type | Sensible Effectiveness (%) | OA Temp (degree F) | RA Temp (degree F) | SA Temp (degree F) | Total Effectiveness (%) | Supplemental heating type | Supplemental heating fuel
07- 782313-1 | Yes | MAU-1 | Scott Springfield | Custom Unit | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
07- 782313-1 | Yes | DOAS-CS | Scott Springfield | Custom Unit | 6815 | 5840 | 12.1 | BHP |  | 0.66 |  |  |  | 0.66 | heat pump | electric
07- 782313-1 | Yes | DOAS-K | Trane | Horizon ASHP | 3830 | 3200 | 6.53 | BHP |  | 0.66 |  |  |  | 0.64 | heat pump | electric
07- 782313-1 | Yes | DOAS-K2 | Trane | Horizon ASHP | 6550 | 6400 | 14.19 | BHP |  | 0.66 |  |  |  | 0.61 | heat pump | electric
07- 782313-1 | Yes | DOAS-P | Trane | Horizon ASHP | 1375 | 1430 | 2.24 | BHP |  | 0.66 |  |  |  | 0.7 | heat pump | electric
09- 581175-1 | Yes | Unknown | Daikin | Unknown | 1900 | 1400 | 2.3 | Fan HP |  | Unknown |  |  |  | Unknown | heat pump | Electric
11- 531122-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
11- 631833-2 | Yes | MAU-1 | Greenheck | IGX-112-H22 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
11- 631833-2 | Yes | RTU-1 | TRANE | OAKD210A4-D1A1A0JR-A1K02AF1JR-O61B00401 | 7400 | 7400 | 7 | BHP | Direct | 0.65 |  |  |  | Unknown | gas-fired | Gas
11- 631833-2 | Yes | RTU-2 | TRANE | OAKD210A4-D1A1A0JR-A1K02AF1JR-O61B00401 | 7400 | 7400 | 7 | BHP | Direct | 0.65 |  |  |  | Unknown | gas-fired | Gas
11- 656138-1 | Yes | DOAS-1 | Addison | PROA-120-C2XL | 4285 | 4285 | 6 | Fan HP | Calculated | 0.28863 | 5.4 | 74 | 25.2 | Unknown | gas-fired | Gas
11- 656138-1 | Yes | DOAS-2 | Addison | PROA-120-C2XL | 4750 | 4750 | 9 | Fan HP | Calculated | 0.38192 | 5.4 | 74 | 31.6 | Unknown | gas-fired | Gas
13- 404186-1 | Yes | DOAS-R-1 | Daikin | OPS020A | 5500 | 5500 | 9.81 | BHP | Direct | 0.66 |  |  |  | 0.65 | electric coil | electric
13- 404186-1 | Yes | ERV-4-1 | Renewaire | EV450IN | 300 | 300 | 1 | Fan HP | Direct | 0.66 |  |  |  | Unknown | electric coil | electric
13- 636582-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 426751-1 | Yes | HRV-1 | Lossnay | LGH-F1200 | 850 | 625 | Unknown |  | Calculated | 0.7793 | 7 | 70 | 43.1 | Unknown | electric coil | electric
14- 426751-1 | Yes | HRV-2 | Aldes | HRV 500DDD | 200 | 200 | Unknown |  | Calculated | 0.38889 | 7 | 70 | 31.5 | Unknown | electric coil | electric
14- 493663-2 | Yes | HRU-L1 | Daikin | RPS025D | 12000 |  | 13.14 | BHP |  | Unknown |  |  |  | 0.81 | gas-fired | Gas
14- 494803-1 | Yes | ERV-1 | Greenheck | RVE-50-46P-30H-12.5 | 2600 | 2875 | 3.5 | Fan HP | Direct | 0.748 |  |  |  | Unknown | gas-fired | Gas
14- 494803-1 | Yes | ERV-2 | Greenheck | RVE-35-30P-30L-5 | 975 | 1075 | 2 | Fan HP | Direct | 0.817 |  |  |  | Unknown | gas-fired | Gas
14- 494803-1 | Yes | ERV-3 | Panasonic | FV-04VE1 | 40 | 40 | 0.03 | BHP | Direct | 0.66 |  |  |  | Unknown | Unknown | Unknown
14- 526453-1 [DHP] | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 540112-1 [Corridors\Main Floor Areas] | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 540112-1 [Corridors\Main Floor Areas] | Yes | RTU-1 | AAON | RQ-004 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | gas
14- 540112-1 [Misc.] | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 550027-2 | Yes | DOAS-A | Greenheck | ERCH-90-30L | 6525 | 4515 | 8 | Fan HP |  | Unknown |  |  |  | 0.63 | gas-fired | gas
14- 550027-2 | Yes | DOAS-B | Greenheck | ERCH-90-30L | 5570 | 4545 | 8 | Fan HP |  | Unknown |  |  |  | 0.671 | gas-fired | Gas
14- 550027-2 | Yes | DOAS-C | Greenheck | ERCH-90-30L | 7265 | 5785 | 8 | Fan HP |  | Unknown |  |  |  | 0.671 | gas-fired | Gas
14- 550027-2 | Yes | DOAS-D | Greenheck | ERCH-45-15H | 3215 | 3215 | 8 | Fan HP |  | Unknown |  |  |  | 0.773 | gas-fired | Gas
14- 550027-2 | Yes | MAU-K | DGX-118-H32 | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | electric
14- 673795-2 | Yes | SAU-1 | Trane | UCCA-12 | 5900 | 5000 | 7.832 | BHP | Calculated | 0.52723 | 23 | 70 | 44 | Unknown | hot water coil | Gas
14- 587282-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 587282-1 | Yes | MAU-1 | Modine | HDG 350 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
14- 587282-1 | Yes | MAU-2 | Modine | HDG 350 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
14- 611061-1 | Yes | MUA-1 | Greenheck | IGX-109-H12 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
14- 626014-1 | Yes | ERV-1 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | electric coil | Electric
14- 626014-1 | Yes | ERV-2 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | electric coil | Electric
14- 626014-1 | Yes | ERV-3 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | electric coil | Electric
14- 626014-1 | Yes | ERV-4 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | electric coil | Electric
14- 626014-1 | Yes | AHU-3 | York | ZF078 | 2700 | 2700 | 1.5 | Fan HP |  | Unknown |  |  |  | Unknown | gas-fired | Gas
14- 626014-1 | Yes | AHU-4 | York | ZF078 | 2700 | 2700 | 1.5 | Fan HP |  | Unknown |  |  |  | Unknown | gas-fired | Gas
14- 626014-1 | Yes | MAU-1 | CaptiveAire | A4-D.1000-920 | 8000 | 8000 | 5 | Fan HP |  | Unknown |  |  |  |  | gas-fired | Gas
14- 634379-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 662676-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
14- 668269-1 | Yes | DOAS 1.R.01 | Innovent | ERU-OU-PL-10000-FF-IF-IV-460 | 10000 | 10000 | 17.86 | BHP | Calculated | 0.63636 | 26 | 70 | 54 | 0.89 | gas-fired | Gas
14- 668269-1 | Yes | DOAS 1.R.02 | Innovent | ERU-OU-PL-10000-FF-IF-IV-460 | 10000 | 10000 | 17.86 | BHP | Calculated | 0.63636 | 26 | 70 | 54 | 0.89 | gas-fired | Gas
14- 668269-1 | Yes | DOAS 2.R.01 | Innovent | ERU-OU-PL-11000-FF-IF-IV-460 | 11000 | 11000 | 19.48 | BHP | Calculated | 0.63636 | 26 | 70 | 54 | 0.89 | gas-fired | Gas
14- 668269-1 | Yes | DOAS 2.R.02 | Innovent | ERU-OU-PL-11000-FF-IF-IV-460 | 11000 | 11000 | 19.48 | BHP | Calculated | 0.63636 | 26 | 70 | 54 | 0.89 | gas-fired | Gas
14- 668269-1 | Yes | DOAS 3.R.01 | Innovent | ERU-OU-PL-15400-FF-IF-IV-460 | 15400 | 15400 | 27.21 | BHP | Calculated | 0.63636 | 26 | 70 | 54 | 0.89 | gas-fired | Gas
14- 731874-1 [RTU] | Yes | HRU-1 | Greenheck | ERCH-20 | 1285 | 1495 | 2.5 | Fan HP | Calculated | Unknown | 2 | 70 | 56 | Unknown | gas-fired | Gas
14- 731874-1 [RTU] | Yes | HV-1 | Modine | HDP800 | 6300 | 6300 | 5 | Fan HP | Calculated | Unknown | -2 | 70 | 92.1 | Unknown | gas-fired | Gas
15- 419460-1 | Yes | ERV-1 | Renewaire | EV-200 | 160 | 160 | Unknown |  | Calculated | Unknown | 22 | 70 | Unknown | Unknown | Unknown | Unknown
15- 419460-1 | Yes | ERV-2 | Renewaire | EV-200 | 160 | 160 | Unknown |  | Calculated | Unknown | 22 | 70 | Unknown | Unknown | Unknown | Unknown
15- 419460-1 | Yes | ERV-4 | Renewaire | EV-200 | 160 | 160 | Unknown |  | Calculated | Unknown | 22 | 70 | Unknown | Unknown | Unknown | Unknown
15- 419460-1 | Yes | ERV-3 | Renewaire | EV-200 | 280 | 325 | Unknown |  | Calculated | Unknown | 22 | 70 | Unknown | Unknown | Unknown | Unknown
15- 425673-1 | Yes | ERV-1 | Renewaire | HE2XRT | 1500 | 1500 | 1.8 | BHP | Calculated | Unknown | 17 | 0 | 54 | Unknown | electric coil | Electric
15- 425673-1 | Yes | ERV-2 | Mitsubishi | LGH | 470 | 470 | 0.72 | BHP |  | Unknown | Unknown | 70 | 54 | 0.69 | electric coil | Electric
15- 425673-1 | Yes | MAU-1 | Greenheck | IG | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
15- 458201-1 | Yes | DOA-1 | AAON | RN | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | gas
15- 458201-1 | Yes | DOA-2 | AAON | RN | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | gas
15- 464466-1 | Yes | ERV-1 | Renewaire | HE1.5XINH | 1200 | 1200 | 2 | Fan HP | Direct | 0.68 |  |  |  | 0.6 | None | None
15- 464466-1 | Yes | ERV-2 | AAON | RN-016-8-0-0000-549 | 4175 | 3925 | 6 | Fan HP | Direct | 0.68 |  |  |  | 0.6 | gas-fired | gas
15- 464466-1 | Yes | ERV-3 | AAON | RN-016-8-0-0000-549 | 3931 | 3951 | 5 | Fan HP | Direct | 0.68 |  |  |  | 0.6 | gas-fired | gas
15- 580950-1 | Yes | DOAS-R-1 | York | XTI | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | heat pump | electric
15- 602446-1 | Yes | ERV-1 | Mitsubishi | LGH-F300RX5-E | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | Unknown | Unknown
15- 602446-1 | Yes | MAU-1 | Trane | GRCA40 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
03- 779006-1 | Yes | RTU-1 | Daikin | DPS007A | 2840 | 2840 | 6 | Fan HP | Calculated | 0.60417 | 22 | 70 | 51 | Unknown | gas-fired | Gas
15- 700290-1 | Yes | MAU-1 | CaptiveAire | A4-D.1000-920 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 400924-1 | Yes | MAU-1 | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 404663-1 | Yes | MAU-1 | CaptiveAire | A2-D.250-20D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
16- 438381-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
16- 490400-1 | Yes | ERV-1 | Renewaire | HE1XRTH-ECM | 360 | 360 | 1 | Fan HP | Direct | 0.7 |  |  |  | Unknown | Unknown | Unknown
14- 730160-1 | Yes | ERV 1 | Daikin | CAH013GVDM | 5800 | 5200 | 12.5 | Fan HP | Calculated | 0.82857 | 0 | 70 | 52 | 0.74 | Unknown | Electric
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | Yes | HVU-1 | Daikin | CAH020GVGM | 7965 | 7965 | 15 | Fan HP | Direct | 0.65 |  |  |  | 0.62 | gas-fired | Gas
15- 419203-1 [Gym, Cafeteria, North Wing, South Wing] | Yes | HVU-2 | Daikin | CAH015GVGM | 5660 | 5660 | 10 | Fan HP | Direct | 0.62 |  |  |  | 0.59 | gas-fired | Gas
16- 514976-1 | Yes | MAU-1 | Greenheck | DGX-115-H32 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 536718-1 | Yes | ERV-1 | Renewaire | HE2XRT | 1630 | 1080 | 3 | Fan HP |  | Unknown |  |  |  | 0.74 | electric coil | Electric
16- 536718-1 | Yes | ERV-2 | Renewaire | HE1XRT | 800 | 800 | 1.5 | Fan HP |  | Unknown |  |  |  | 0.585 | electric coil | Electric
16- 536718-1 | Yes | ERV-3 | Renewaire | HE1XRT | 830 | 540 | 1.5 | Fan HP |  | Unknown |  |  |  | 0.55 | electric coil | Electric
16- 536718-1 | Yes | MAU-1 | Alton | 45MU-100-15-2 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
16- 537171-1 | Yes | DOAS R-4 | Energy Labs | Unknown | 12500 | 12500 | 23 | BHP | Calculated | 0.73333 | 25 | 70 | 58 | 0.72 | heat pump | Electric
16- 537171-1 | Yes | DOAS R-1 | Energy Labs | Unknown | 12500 | 12500 | 23 | BHP | Calculated | 0.73333 | 25 | 70 | 58 | 0.72 | heat pump | Electric
16- 537171-1 | Yes | DOAS R-2 | Energy Labs | Unknown | 8000 | 8000 | 17 | BHP | Calculated | 0.68889 | 25 | 70 | 56 | 0.67 | heat pump | Electric
16- 537171-1 | Yes | DOAS R-3 | Energy Labs | Unknown | 8000 | 8000 | 17 | BHP | Calculated | 0.68889 | 25 | 70 | 56 | 0.67 | heat pump | Electric
16- 537171-1 | Yes | MAUR-1 | Greenheck | QUID | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
16- 558605-2 | Yes | ERV-1 | LG | ARVU093ZFA2 | 883 | 883 | Unknown |  |  | Unknown |  |  |  | Unknown | Unknown | Unknown
16- 621440-1 | Yes | ERV-1 | Clean Comfort | VE70220 | 150 | 150 | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | Gas
16- 640402-1 | Yes | ERV-1 | Renewaire | EV130 | 80 | 80 | Unknown |  |  | Unknown |  |  |  | 0.67 | Unknown | Unknown
16- 657491-1 | Yes | MAU-1 | Greenheck | DGX-109-H12 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 657491-1 | Yes | MAU-2 | Greenheck | DGX-109-H12 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 662436-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | 4 | Fan HP |  | Unknown |  |  |  |  | Unknown | Unknown
16- 688717-1 [VRF] | Yes | MAU-1 | Daikin | DPS007A | 1875 | 1875 | 2.3 | Fan HP | Calculated | Unknown | 0 | 70 | 54 |  | gas-fired | Gas
16- 688717-1 [VRF] | Yes | MAU-2 | Daikin | DPS005A | 1295 | 1295 | 1.3 | Fan HP | Calculated | Unknown | 0 | 70 | 55 |  | gas-fired | Gas
16- 706094-1 | Yes | DOAS-701 | AAON | N/A | 20000 | 18000 | 30 | Fan HP | Calculated | 0.66667 | 20 | 70 | 50 | 0.577 | None | None
16- 720532-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
16- 727455-1 | Yes | MAU-1 | Greenheck | DGK | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
15- 640275-1 [Common Areas and Corridors] | Yes | HRV-1 | Aldes | H1800A-FI | 1400 | 1400 | Unknown |  | Calculated | 0.4 | 15 | 70 | 37 | 0.35 | Unknown | Unknown
15- 640275-1 [Common Areas and Corridors] | Yes | MAU-1 | CaptiveAire | A1-D.500-G10 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 429395-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
17- 571695-2 | Yes | ERV-1 | LOSSNAY | LGH-F470RX5-E1 | 400 | 415 | 0.5 | Fan HP | Direct | 0.62 |  |  |  | 0.66 | Unknown | Unknown
17- 571695-2 | Yes | ERV-2 | LOSSNAY | LGH-F600RX5-E1 | 600 | 540 | 0.5 | Fan HP | Direct | 0.61 |  |  |  | 0.63 | Unknown | Unknown
17- 571695-2 | Yes | ERV-3 | LOSSNAY | LGH-F600RX5-E1 | 510 | 460 | 0.5 | Fan HP | Direct | 0.61 |  |  |  | 0.63 | Unknown | Unknown
17- 571695-2 | Yes | ERV-4 | LOSSNAY | LGH-F600RX5-E1 | 590 | 600 | 0.5 | Fan HP | Direct | 0.64 |  |  |  | 0.67 | Unknown | Unknown
17- 571695-2 | Yes | ERV-5 | LOSSNAY | LGH-F600RX5-E3 | 540 | 600 | 0.5 | Fan HP | Direct | 0.66 |  |  |  | 0.69 | Unknown | Unknown
17- 571695-2 | Yes | ERV-6 | LOSSNAY | LGH-F470RX5-E1 | 390 | 470 | 0.5 | Fan HP | Direct | 0.6 |  |  |  | 0.62 | Unknown | Unknown
17- 571695-2 | Yes | ERV-7 | LOSSNAY | LGH-F600RX5-E1 | 590 | 540 | 0.5 | Fan HP | Direct | 0.63 |  |  |  | 0.66 | Unknown | Unknown
17- 571695-2 | Yes | ERV-8 | LOSSNAY | LGH-F470RX5-E1 | 360 | 470 | 0.5 | Fan HP | Direct | 0.71 |  |  |  | 0.74 | Unknown | Unknown
17- 571695-2 | Yes | ERV-9 | LOSSNAY | LGH-F600RX5-E1 | 590 | 530 | 0.5 | Fan HP | Direct | 0.6 |  |  |  | 0.62 | Unknown | Unknown
17- 571695-2 | Yes | ERV-10 | LOSSNAY | LGH-F470RX5-E1 | 410 | 360 | 0.5 | Fan HP | Direct | 0.6 |  |  |  | 0.62 | Unknown | Unknown
17- 571695-2 | Yes | ERV-11 | LOSSNAY | LGH-F600RX5-E1 | 600 | 560 | 0.5 | Fan HP | Direct | 0.62 |  |  |  | 0.64 | Unknown | Unknown
17- 584823-1 | Yes | AHU-04-CC | Thermal | FP | 11000 | 11000 | Unknown |  |  | Unknown |  |  |  | Unknown | electric coil | electric
17- 584823-1 | Yes | AHU-04-N | Thermal | FP | 10000 | 10000 | Unknown |  |  | Unknown |  |  |  | Unknown | electric coil | electric
17- 584823-1 | Yes | AHU-04-S | Thermal | FP | 4500 | 4500 | Unknown |  |  | Unknown |  |  |  | Unknown | electric coil | electric
17- 635582-1 | Yes | MAU-1 | CaptiveAire | Unknown | Unknown | Unknown | 4 | Fan HP |  | Unknown |  |  |  |  | Unknown | Unknown
17- 642436-1 | Yes | MAU-1 | CaptiveAire | A1-D250-G10 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 505459-1 | Yes | ERU-1 | VENMAR | VENMAR MODEL VHC-36 | 2000 | 2000 | 3.08 | Fan HP | Direct | Unknown |  |  |  | Unknown | Unknown | Unknown
16- 507255-1 [Corridors] | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
17- 697310-1 | Yes | DH-B2-1 | Greenheck | IDHC | 600 | 600 | 0.34 | Fan HP | Direct | 0.69 |  |  |  | Unknown | Unknown | Electric
17- 697310-1 | Yes | DH-B2-2 | Greenheck | IDHC | 615 | 615 | 0.34 | Fan HP | Direct | 0.69 |  |  |  | Unknown | Unknown | Electric
17- 697310-1 | Yes | ERV-B2-1 | Mitsubishi | Lossnay LGH600 | 600 | 600 | 0.34 | Fan HP | Direct | 0.69 |  |  |  | 0.69 | Unknown | Electric
17- 697310-1 | Yes | ERV-B2-2 | Mitsubishi | Lossnay LGH600 | 615 | 615 | 0.34 | Fan HP | Direct | 0.69 |  |  |  | 0.69 | Unknown | Electric
17- 716517-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
16- 640577-1 | Yes | MAU-1 | AAON | RN Series | 3000 | 3000 | 1.87 | BHP | Calculated | Unknown | 81 |  | 55 | 0.88 | gas-fired | Gas
16- 640577-1 | Yes | MAU-2 | AAON | RN Series | 1720 | 1720 | 1.89 | BHP | Calculated | Unknown | 81 |  | 56 | 0.88 | gas-fired | Gas
17- 777891-1 [Common area] | Yes | AERV-1 | Pennbarry | G036 | 3540 | 2630 | 8 | Fan HP |  | Unknown |  |  |  | 0.853 | gas-fired | gas
17- 777891-1 [Common area] | Yes | AERV-2 | Pennbarry | G036 | 3570 | 2630 | 8 | Fan HP |  | Unknown |  |  |  | 0.853 | gas-fired | gas
17- 777891-1 [Common area] | Yes | AMAU-1 | CaptiveAire | A1-d.250-G10 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | gas
17- 792314-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
17- 803573-1 [Misc.] | Yes | ERV-1 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | Unknown | Unknown
17- 803573-1 [Misc.] | Yes | ERV-2 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | Unknown | Unknown
17- 803573-1 [Misc.] | Yes | ERV-3 | Mitsubishi | LGH-F600RX5 | 600 | 600 | Unknown |  |  | Unknown |  |  |  | 0.57 | Unknown | Unknown
17- 808067-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
16- 735523-1 [Classrooms, commons, misc.] | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
17- 813087-1 | Yes | MAU-1 | CaptiveAire | A1-D250-G10-MPU | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
17- 813087-1 | Yes | ERU-1 | AAON | RN-009 | 3030 | 3360 | 6 | Fan HP | Calculated | 0.55825 | 9 | 72 | 48 | Unknown | gas-fired | Gas
17- 813087-1 | Yes | ERU-2 | AAON | RN-016 | 3880 | 2900 | 7 | Fan HP | Calculated | 0.76453 | 9 | 72 | 45 | Unknown | gas-fired | Gas
17- 813087-1 | Yes | ERU-3 | AAON | RN-009 | 2270 | 2730 | 5 | Fan HP | Calculated | 0.56753 | 9 | 72 | 52 | Unknown | gas-fired | Gas
17- 815466-1 | Yes | ERV-1 | Greenheck | ERCH-55-30L-IG-01 | 4750 | 4750 | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | Gas
17- 821806-1 | Yes | OSA-1 | Stelpro | MUAA101021 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | electric coil | electric
17- 821806-1 | Yes | MAU-1 | Stelpro | MUAA121621 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
17- 821806-1 | Yes | MAU-2 | Thermolec | FER-08-240/1 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
17- 832860-1 [Living area] | Yes | ERV-1 | Renewaire | HE2XRT | 1225 | 875 | 3.5 | Fan HP | Direct | 0.6 |  |  |  | 0.6 | Unknown | Unknown
17- 855496-1 [Living] | Yes | ERV-1 | Renewaire | EV450RT | 200 | 370 | 1 | BHP | Calculated | 0.50193 | 0 | 70 | 65 | Unknown | Unknown | Unknown
17- 855496-1 [Living] | Yes | ERV-2 | Renewaire | HE1XRT | 500 | 700 | 1 | BHP | Calculated | 0.60204 | 0 | 70 | 59 | Unknown | Unknown | Unknown
17- 855496-1 [Living] | Yes | ERV-3 | Renewaire | EV90 | 40 | 70 | 0.3 | BHP | Calculated | 0.54694 | 0 | 70 | 67 | Unknown | Unknown | Unknown
17- 856087-1 | Yes | ERV-1 | LG | ARVU093ZFA2 | 800 | 800 | Unknown |  | Direct | 0.65 |  |  |  | Unknown | electric | electric
17- 856087-1 | Yes | MAU-1 | Accurex | XDG-112-H20 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
17- 866279-1 | Yes | MAU-1 | CaptiveAire | A3-D.500-20D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
17- 686039-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
18- 560625-1 | Yes | MAU-1 | CaptiveAire | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
18- 576787-1 | Yes | ERV | Greenheck | ECV-10-VG | 900 | 750 | 1 | Fan HP |  | Unknown |  |  |  | 0.555 | Unknown | Unknown
18- 585712-1 | Yes | ERV-1 | Renewaire | HE2XINV | 1680 | 1680 | 3 | Fan HP | Direct | 0.64 |  |  |  | Unknown | electric coil | electric
18- 585712-1 | Yes | ERV-2 | Renewaire | EV450RT | 450 | 450 | 1 | Fan HP | Direct | 0.68 |  |  |  | Unknown | electric coil | electric
18- 585712-1 | Yes | ERV-3 | Renewaire | HE4XINV | 2500 | 2600 | 6 | Fan HP | Direct | 0.7 |  |  |  | Unknown | electric coil | electric
18- 585712-1 | Yes | MAU-1 | CaptiveAire | A1-E.274-G10 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
18- 612115-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 641081-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 650512-1 | Yes | AHU-R01 | Xetex | IAQ | 8460 | 8460 | 19.3 | BHP |  | Unknown |  |  |  | 0.751 | electric coil | Electric
18- 650512-1 | Yes | AHU-R02 | Xetex | IAQ | 8460 | 8460 | 19.3 | BHP |  | Unknown |  |  |  | 0.751 | electric coil | Electric
18- 596289-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 704117-1 | Yes | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | Unknown | Unknown
18- 704117-1 | Yes | DOAS-1 | Venmar | Custom | 18500 | 18500 | 17 | Fan HP |  | Unknown |  |  |  | 0.75 | Unknown | electric
18- 718226-1 [AHU] | Yes | ERV-1 | Greenheck | Pve-35 | 3170 | 3170 | 5 | BHP | Calculated | 0.63231 | -1.8 | 70 | 43.6 | Unknown | Unknown | Unknown
18- 718226-1 [AHU] | Yes | ERV-2 | Greenheck | Pve-20 | 1575 | 1425 | 1.5 | HP | Calculated | 0.72966 | -1.8 | 70 | 45.6 | Unknown | Unknown | Unknown
18- 718226-1 [AHU] | Yes | ERV-3 | Greenheck | Pve-35 | 2600 | 1875 | 2.6 | BHP | Calculated | 0.89805 | -1.8 | 70 | 44.7 | Unknown | Unknown | Unknown
18- 718226-1 [AHU] | Yes | ERV-4 | Greenheck | Pve-20 | 2050 | 2050 | 2.4 | BHP | Calculated | 0.62953 | -1.8 | 70 | 43.4 | Unknown | Unknown | Unknown
18- 718226-1 [AHU] | Yes | OAU-K | AAON | RN-040 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | gas-fired | Gas
18- 718902-1 | Yes | HRV-1 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-3 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-4 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-5 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-6 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-7 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-8 | Daikin | VAM1200GVJU | 1200 | 1200 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 718902-1 | Yes | HRV-9 | Daikin | VAM1200GVJU | 600 | 600 | Unknown |  | Calculated | 0.76923 | 26 | 65 | 56 | Unknown | Unknown | Unknown
18- 723839-1 | Yes | DOAS-1 | AAON | RN-009 | 2735 | 2000 | 5 | BHP |  | Unknown |  |  |  | Unknown | electric coil | Electric
18- 723839-1 | Yes | MAU-1 | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
18- 737861-1 | Yes | DOAS-1 | AAON | RN-020-8-0-BA02-38B | 4665 | 4665 | 2.45 | BHP | Unknown | Unknown |  |  |  | Unknown | gas-fired | Gas
18- 737861-1 | Yes | DOAS-2 | AAON | RN-025-8-BA02-3CB | 5445 | 5445 | 3.03 | BHP | Unknown | Unknown |  |  |  | Unknown | gas-fired | Gas
18- 811956-1 | Yes | ERV-1 | Renewaire | EV130 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  | Unknown | Unknown | Unknown
19- 700419-1 | Yes | MAU-1 | CaptiveAire | A3-D.750-24D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
19- 731945-1 | Yes | HRU-1 | AAON | Unknown | 4400 | 3300 | 7 | Fan HP | Calculated | 0.7619 | 0 | 70 | 40 | Unknown | electric coil | Electric
19- 731945-1 | Yes | HRU-2 | AAON | Unknown | 4700 | 4300 | 8 | Fan HP | Calculated | 0.70266 | 0 | 70 | 45 | Unknown | electric coil | Electric
19- 731945-1 | Yes | HRU-3 | AAON | Unknown | 2000 | 1600 | 5 | Fan HP | Calculated | 0.75 | 0 | 70 | 42 | Unknown | electric coil | Electric
19- 731945-1 | Yes | HRU-4 | AAON | Unknown | 2650 | 2650 | 5 | Fan HP | Calculated | 0.62857 | 0 | 70 | 44 | Unknown | electric coil | Electric
18- 596300-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
19- 765123-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
19- 506267-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 625974-1 | Yes | MAU-1 | Trane | OAGD120F3 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
18- 625974-1 | Yes | MAU-2 | Trane | OAGD120F3 | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
18- 554364-1 [Administrative] | Yes | ERU-1 | Cook | ERV-4500 | 3510 | 3025 | 3.5 | Fan HP | Calculated | 0.81776 | 9 | 72 | 53.4 | 0.784 | Unknown | Unknown
18- 554364-1 [Kitchen & Whitebox] | Yes | MAU-1 | CaptiveAire | A3-D.500-24D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 554364-1 [Kitchen & Whitebox] | Yes | MAU-2 | CaptiveAire | A2-D.250-20D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 554364-1 [Kitchen & Whitebox] | Yes | MAU-3 | CaptiveAire | A2-D.500-20D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
11- 556107-1 | Yes | DOAS-1 | AAON | RN-020-3-0-EA-389 | 8000 | 8000 | 20 | Fan HP | Calculated | 0.58 | 20 | 70 | 49 | Unknown | gas-fired | Gas
16- 442030-1 | Yes | ERV-1-1 | Renewaire | HE1XINH | 560 | 560 | 1 | Fan HP |  | Unknown |  |  |  | Unknown | Unknown | Unknown
16- 442030-1 | Yes | RTU-R-1 | AAON | RQ-006 | 2400 | 2400 | 1.8 | BHP |  | Unknown |  |  |  | Unknown | electric coil | Electric
16- 442030-1 | Yes | RTU-R-2 | AAON | RQ-006 | 2400 | 2400 | 1.8 | BHP |  | Unknown |  |  |  | Unknown | electric coil | Electric
16- 615127-1 | Yes | ERV-1 | LG | ARVU123ZFA2 | 1100 | 1100 | Unknown |  | Calculated | Unknown | 20 | 70 |  | 0.588 | Unknown | Unknown
16- 615127-1 | Yes | ERV-2 | LG | ARVU123ZFA2 | 900 | 900 | Unknown |  | Calculated | Unknown | 20 | 70 |  | 0.615 | Unknown | Unknown
16- 615127-1 | Yes | ERV-3 | LG | ARVU123ZFA2 | 1100 | 1100 | Unknown |  | Calculated | Unknown | 20 | 70 |  | 0.588 | Unknown | Unknown
08- 723130-1 | Yes | ERV | LG | ARVU123ZFA2 | 1150 | 1100 | Unknown |  | Direct | Unknown |  |  |  | 0.58 | Unknown | Electric
08- 723130-1 | Yes | ERV-1 | LG | ARVU123ZFA2 | 1150 | 1100 | Unknown |  | Direct | 0.58 |  |  |  | Unknown | electric coil | Electric
18- 614250-1 | Yes | DOAS-R1 | Greenheck | ERCH-20 | 1720 | 2075 | 6 | Fan HP | Calculated | 0.66313 | 24.5 | 70 | 60.9 | 0.623 | hot water coil | Gas
18- 614250-1 | Yes | DOAS-R2 | Greenheck | ERCH-20 | 1485 | 1485 | 3 | Fan HP | Calculated | 0.83736 | 24.5 | 70 | 62.6 | 0.786 | hot water coil | Gas
18- 614250-1 | Yes | DOAS-R3 | Greenheck | ERCH-20 | 1000 | 1440 | 1.5 | Fan HP | Calculated | 0.66239 | 24.5 | 70 | 67.9 | 0.626 | hot water coil | Gas
18- 535655-1 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
18- 563561-1 | Yes | G-RTU-4B | Micrometl | EVEDEEH39X0A0AAEF | 2500 | 2500 | 7.5 | Fan HP | Calculated | 0.71212 | 6 | 72 | 53 | 0.72 | gas-fired | Gas
18- 563561-1 | Yes | G-RTU-5B | Micrometl | EVHFEEH39X0A0AAEF | 3200 | 3200 | 7.5 | Fan HP | Calculated | 0.74242 | 6 | 72 | 55 | 0.75 | gas-fired | Gas
17- 551538-3 | Yes | ERV-1 | Renewaire | HE3XRT | 3150 | 2900 | 6 | Fan HP | Direct | 0.63 |  |  |  | 0.41 | Unknown | Unknown
17- 701880-1 | Yes | ERV-01 | Renewaire | EV450RT | 350 | 350 | 1 | Fan HP | Calculated | 0.71429 | 0 | 70 | 50 | Unknown | Unknown | Unknown
17- 701880-1 | Yes | ERV-02 | Panasonic | FV-10VEC1 | 60 | 60 | 1.6 | Fan HP |  | Unknown |  |  |  | Unknown | Unknown | Unknown
17- 701880-1 | Yes | ERV-03 | Panasonic | FV-10VEC1 | 100 | 100 | 0.8 | Fan HP |  | Unknown |  |  |  | Unknown | Unknown | Unknown
18- 863366-1 | Yes | MAU-1 | CaptiveAire | A2-D.250-20D | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | gas-fired | gas
14- 689118-1 | Yes | MAU-1 | Carrier | 48P2L03561 | 14000 | 14000 | 18 | Fan HP |  | Unknown |  |  |  | 0.81 | gas-fired | Gas
14- 689118-1 | Yes | MAU-2 | Carrier | 48TCSD14A1A6-6F3G1 | 5000 | 5000 | 3 | Fan HP |  | Unknown |  |  |  | 0.82 | gas-fired | Gas
17- 550764-1 | Yes | ERV-101 | Renewaire | HE1.5XINH | 1100 | 1100 | 2 | Fan HP | Direct | 0.7 |  |  |  | Unknown | electric coil | Electric
17- 550764-1 | Yes | ERV-102 | Renewaire | EV300 | 300 | 300 | 0.4 | Fan HP | Direct | 0.7 |  |  |  | Unknown | electric coil | Electric
17- 550764-1 | Yes | MAU-101 | Greenheck | MSCF | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | electric coil | electric
17- 550764-1 | Yes | HRU-401 | Daikin | Unknown | 3500 | 3500 | 4.8 | BHP | Direct | 0.63 |  |  |  | Unknown | electric coil | Electric
17- 550764-1 | Yes | HRU-501 | Daikin | Unknown | 3500 | 3500 | 4.8 | BHP | Direct | 0.63 |  |  |  | Unknown | electric coil | Electric
17- 550764-1 | Yes | HRU-502 | Daikin | Unknown | 4000 | 4000 | 6.2 | BHP | Direct | 0.59 |  |  |  | Unknown | electric coil | Electric
15- 568036-2 | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  |  | Unknown |  |  |  |  | Unknown | Unknown
19- 550436-1 | Yes | AHU-1 | GREENHECK | Unknown | 12000 | 12000 | 12.37 | BHP |  | Unknown |  |  |  | 0.92 | gas-fired | Gas
19- 550436-1 | Yes | ERV-1 | Trane | Horizon OABD036D3 | 1325 | 1417 | 5 | Fan HP | Calculated | 0.70697 | 2 | 68 | 51.9 | 0.77 | gas-fired | Gas
19- 550436-1 | Yes | ERV-2 | Trane | Horizon OABD036D3 | 1325 | 1417 | 5 | Fan HP | Calculated | 0.70697 | 2 | 68 | 51.9 | 0.77 | gas-fired | Gas

## PopulationSummary
Population Summary
Sample Frame Domain | Total Construction Value | Population (Number of Projects) | n (Final Sample) | Total Estimated Conditioned Square Footage | Relative Precision by Domain
East-Assembly | 1166645 | 242 | 17 | 2943603.5417 | 1.721%
East-Hospital | 767352 | 65 | 18 | 1941332.5472 | 5.654%
East-Lodging | 1180046 | 127 | 14 | 4187148.8595 | 1.477%
East-Multi-Family Residential | 1114280 | 161 | 12 | 6582584.1168 | 13.53%
East-Office | 3230512 | 539 | 15 | 34833607.0706 | 0.5717%
East-Other | 381714 | 102 | 13 | 2424052.397 | 9.84%
East-Residential Care | 243677 | 41 | 8 | 1796718.6385 | 2.938%
East-Restaurant | 121068 | 132 | 15 | 702040.7337 | 24.78%
East-Retail | 537032 | 242 | 17 | 5274569.1333 | 23.87%
East-School (K-12) | 3454709 | 359 | 17 | 13023181.4016 | 3.954%
East-School (University) | 1182379 | 122 | 13 | 3986771.7794 | 1.967%
West-Assembly | 4032009 | 401 | 15 | 11844576.1375 | 53.63%
West-Hospital | 1855652 | 91 | 21 | 4057780.7642 | 2.659%
West-Lodging | 3927031 | 223 | 22 | 16771386.3604 | 17.29%
West-Multi-Family Residential | 17404619 | 977 | 18 | 83226453.8879 | 13.44%
West-Office | 9388982 | 1113 | 29 | 31281465.5181 | 1.055%
West-Other | 1183709 | 136 | 13 | 1430856.6079 | 25.11%
West-Residential Care | 845336 | 84 | 15 | 6621761.9813 | 6.351%
West-Restaurant | 248256 | 185 | 17 | 3212356.3415 | 22.04%
West-Retail | 1544317 | 540 | 17 | 10910835.3331 | 27.94%
West-School (K-12) | 9566691 | 690 | 17 | 60429385.8195 | 2.551%
West-School (University) | 3309694 | 220 | 22 | 9382298.0871 | 1.659%
Total | 66685710 | 6792 | 365 | 316864767.0577
East of the Cascades | 13379414 | 2132 | 159 | 77695610.2192
West of the Cascades | 53306296 | 4660 | 206 | 239169156.8385
This tab summarizes the extrapolated conditioned square footage of the sample using the data set's cataloged conditioned square footage and a regression estimate using the sample frame's Construction Value.
The full population in this data set comes from the sample frame of 6,792 new construction projects stratified by building type and east or west of the Cascades. The Sampling Plan Memo describes the sample frame in more detail. The team also stratified the sample by project size, using Dodge's Construction Value as a proxy for square footage, due to Dodge's incomplete square footage data.
The team evaluated three approaches to extrapolating the data set's results to the full population using the Construction Value and cataloged square footage. The team chose a regression approach to estimate population conditioned square footage for all domains because it had the lowest relative precision at 90% confidence for most domains and the estimations from the alternatives, a mean and a ratio approach, had overlapping error bands with the regression estimates. While overall the data set achieved good relative precision, users should consider the relative precision when evaluating the representativeness of projects in domains with relative precision higher than 20%.
The team developed sample weights for each project in the sample as the number of projects in the population over the number of projects in the sample, by domain.
Regression Estimate Summary
1. The sample mean is found with the relationship:
Where b is:
The population estimate, Y, is the product of sample mean and the count of cases in the population, N.
The variance of the regression estimate is:
Where f_h is the sampling fraction n_h/N_h and W_h is stratum weight N_h/N.
The regression estimate is expected to be an improvement over alternative estimates because it allows for cases where the line regressing x and y does not go through the origin.
The relative precision at 90% confidence of each estimate is 1.645*sqrt(variance)/population estimate.
Equation Sources:
Equation 7.1, page 189, Statistical Techniques, Cochran
Equation 7.19, page 193, Statistical Techniques, Cochran
Equation 7.61, Statistical Techniques, Cochran