## Slide 1: PTCS®
Air Source Heat Pump
Certification Training
Effective January 1, 2023

## Slide 2: The PTCS Program
Pacific Northwest regional program promoting quality duct sealing and installation of AHRI rated high efficiency heat pumps.
  Measures offered are:
76* participating Pacific Northwest Utilities
2,100* active technicians (April 2016-2021)
118,500* approved HVAC installations since 2006
6.4 million population and 2.5 million housing units in BPA territory
2
PTCS and Prescriptive Duct Sealing Air Source Heat Pump | Variable Speed Heat Pump Ground Source Heat Pump
*As of March 2021

## Slide 3: Day’s Agenda & Logistics
Trainer Introduction
Agenda
  In-class and hands on training schedule
  Exam
Logistics
  Restroom location
  Breaks and lunch
  Review folder contents
Symbols in Presentation
In spec | Best practice | Common inspection failure
Best Practice
3

## Slide 4: Course Content
Section 1: Introduction
Section 2: Sizing
Section 3: Airflow
Section 4: Refrigerant Charge
Section 5: Controls
Section 6: Participation Rules & Paperwork
Section 7: Resources
Certification Exam!
4

## Slide 5: Section 1 of 7: Introduction

## Slide 6: Section 1: Introduction
Why Quality Installation Matters
Equipment Requirements
Think Outside the Box Spec
COP, HSPF and HSPF2
Quality Installation:The Big Four

## Slide 7: Why Quality Installation Matters
Primary goal: System performs at its rated capacity per AHRI
HSPF/SEER and HSPF2/SEER2 assumes system is properly sized with “perfect” airflow and proper refrigerant charge.
Customers get a higher efficient heat pump that is commissioned that qualifies for a third-party quality assurance inspection, has longer equipment life, and a lower electric bill when compared to a typical system.
Regional Power Utilities keep electric rates low, which helps avoid the cost of building new electric power generation.
Section 1: Introduction

## Slide 8: Equipment Requirements
Unit must be AHRI Certified
PTCS Certified: at least 9.0 HSPF/14 SEER, or 7.6 HSPF2/13.4 SEER2
Commissioning, Controls, and Sizing: Below 9.0
HSPF/14 SEER* or 7.6 HSPF2/13.4 SEER2*
* Some utilities do not offer a CC&S measure. Be sure to check with local utility before performing work.
Section 1: Introduction

## Slide 9: Code Compliance
When a technician signs the Certified Technician Application, he or she agrees to “complete all work in accordance with the applicable ordinances, codes, and accepted industry standards…”
Section 1: Introduction

## Slide 10: Think Outside the Box Spec
HSPF(2) (Heating Seasonal Performance Factor(2))
  COP (Coefficient of Performance): Underlying efficiency
    Compressor
    Coils
    Fans (indoor and outdoor)
  Defrost
  Cycling
Section 1: Introduction

## Slide 11: COP and HSPF
COP = heating or cooling out/energy in
(at given outdoor temperature)
HSPF = COP x 3.413
(subtractions made for defrost and cycling losses)
  Avg COP of 2 x 3.413 = HSPF 6.8
  Avg COP of 2.64 x 3.413 = HSPF 9.0
Section 1: Introduction
Reminder…PTCS Certified: At least 9.0 HSPF/14 SEER, 7.6 HSPF2/13.4 SEER2.
Commissioning, Controls, and Sizing: Below 9.0 HSPF/14 SEER, 7.6 HSPF2/13.4 SEER2

## Slide 12: Quality Installation: The Big Four
Sizing
  Balance point sizing: 30 degrees or below
Airflow
  At least 325 and up to 500 CFM/ton (or per manufacturer)
  External static pressure 0.8 IWC (200 Pa) or less
Refrigerant Charge
  Heating:Temperature split
  Cooling: Subcooling
  Optional methods (per manufacturer)
Controls
  Auxiliary heat must not engage when outdoor air temperature is above 35°
Section 1: Introduction

## Slide 13: Commissioning Equipment Needs
DG700, DG1000 or other pressure sensing differential manometers
TrueFlow Plate (preferred method)
Pressure Tap
Temperature Probe
Refrigerant Charge Testing Equipment
Section 1: Introduction

## Slide 14: Equipment Maintenance
Manometers
  Should be recalibrated every two years
  A field calibration check should be completed annually or whenever a gauge has been dropped or damage suspected. This procedure can be found at the link below.
Flow Plates
  Modified and damaged flow plates will give you incorrect readings
  Energy Conservatory can provide gasket replacements
Blower Door and Duct Blaster Fans
  These maintain their calibration unless physical damage occurs to the fan or flow
sensing system. A fan field check procedure can be found at the link below.
  Visit: https://energyconservatory.com/calibration-repair/ for more info.
Section 1: Introduction

## Slide 15: Section 2 of 7: Sizing

## Slide 16: Section 2: Sizing
Load Calculations
  Calculating Heating and Cooling Loads
  Balance Point
Sizing
  Selecting Systems
  Variable Speed Equipment
  BPA Sizing Calculator

## Slide 17: Load Calculations
Both heating and cooling loads must be calculated (Wrightsoft, PTCS calculator, HVAC Sizing Tool etc.)
Heating is typically the dominant load in PNW
Heat pump capacity drops at colder temperatures
Balance point no greater than 30°F
maximizes efficiency without oversizing**
Section 2: Sizing
** Best practice: for a single speed unit, size no lower than 20F

## Slide 18: Heat Pump Balance Point (BP)
Section 2: Sizing

## Slide 19: Single Speed Heat Pump Curves & 30F BP
Section 2: Sizing

## Slide 20: Balance Point Using AHRI Data
Section 2: Sizing
20
25
35
30
40
45
HP HL
15
10
5
0
5 7 9 11 13 15 17 19 21 23 25 27 29 31 33 35 37 39 41 43 45 47 49 51 53 55 57 59 61
Outside Air Temperature (OAT)
BTUs (x1000)
3 Ton HP
17oF
47oF
Single Speed
21,600
34,200

## Slide 21: Variable Speed Equipment
Inverter-driven compressor
Lower operating costs, possible higher up front equipment cost
Higher HSPF/HSPF2 under most circumstances
Typically higher output at 30°F Balance Point
  Home with higher heat loss could use 3-ton VSHP instead of 3.5 ton or higher single-speed heat pump
Section 2: Sizing

## Slide 22: Variable Speed Equipment
Less heat pump cycling above balance point
Over sizing/under sizing concerns
Section 2: Sizing

## Slide 23: Single Speed vs. Variable Speed
47oF
34,200
3 Ton Single Speed and Variable Speed HPs Using AHRI Data
3 Ton HP 17oF
Single Speed 21,600
Variable Speed 27,000
33,000
AHRI Outdoor Conditions
HP Capacities
17oF
47oF
Section 2: Sizing

## Slide 24: BPA’s Heat Pump Sizing Calculator
Location
Vintage
Window Type
Balance Point
Calculated Heat Pump Size
Calculated Design Load
30
Note: Click on above image to link to online calculator
Section 2: Sizing

## Slide 25: BPA’s Heat Pump Sizing Calculator
Section 2: Sizing

## Slide 26: Section 3 of 7: Airflow

## Slide 27: Section 3: Airflow
System Airflow
Definitions
Fan Curves & Equipment Setup
What Creates Resistance?
Duct Sizing
ECM Fan Motor
Measuring Airflow
Low Flow Culprits
Exercise
Supply Air Fan

## Slide 28: System Airflow
Important for energy savings and comfort
Heat transfer (system capacity and efficiency) depends on the flow of air across the indoor unit coil
Measured airflow: at least 325 to 500 CFM/ton or meet
manufacturer’s specifications
  True Flow Plate
  External Static Pressure – CFM manufacturer lookup table
  Duct Blaster pressurization fan matching
External Static Pressure shall not exceed 0.8 Inches H2O or 200 Pa
Note: Duct systems may require modification to meet flow requirements
Section 3: Airflow

## Slide 29: VSHP System Airflow
VSHP Requirement Only – Air Flow: Must be as specified in the heat pump manufacturer’s documentation.Does not need to be measured using TrueFlow plate, External Static Pressure – CFM manufacturer lookup table, or Duct Blaster pressurization fan matching.
VSHP Requirement Only – External Static Pressure:Must be as
specified in the heat pump manufacturer’s documentation.
Section 3: Airflow

## Slide 30: Definition: Static vs. Velocity Pressure
Static Pressure
Exerted in all directions regardless
of direction of air flow.
Flow always high to low static pressure.
Measurement of resistance to flow.
Same pressure type that causes a
balloon or tire to keep its shape.
Measured directly with a static
pressure tap and a manometer.
Velocity Pressure
Directional; only exerted in the
direction of flow.
Causes gravity damper to open
or a sail switch to move.
In a duct, cannot be measured directly: obtained by measuring difference between total pressure and static pressure.
Causes the leaves on a tree to
move in the breeze.
TOTAL PRESSURE
Section 3: Airflow

## Slide 31: Definition: External Static Pressure
-0.19
Filter
Air Handler
Outdoor Unit
MATCHED SYSTEM
Section 3: Airflow
Note: the tap in the return duct needs to be after the filter and before the air handler.
0.16

## Slide 32: Static Pressure Tap
Section 3: Airflow
Point tap into air flow

## Slide 33: Static Pressure Drop and Readings
(-0.38)
Section 3: Airflow
Heat Pump ESP 0.35 Inches H2O
Note: the tap in the return is between the filter and fan.

## Slide 34: Measuring Return Static Pressure
Section 3: Airflow

## Slide 35: Measuring Return Static Pressure
Section 3: Airflow
.280

## Slide 36: Measuring Supply Static Pressure
Section 3: Airflow

## Slide 37: Measuring Supply Static Pressure
Section 3: Airflow
.340

## Slide 38: Measure External Static Pressure
Section 3: Airflow
Step 1
Measure Return Static Pressure (drop negative sign)
Step 2
Measure Supply Static Pressure
Step 3
Calculate External Static Pressure (ESP)
Return + Supply = ESP
Return | Supply | ESP
-0.280 InH2O (drop negative sign) | 0.340 InH2O | 0.280 + 0.340 = 0.620 InH2O
Example:

## Slide 39: Fan Chart
Section 3: Airflow

## Slide 40: Equipment Set Up
Configure blower to deliver 400 CFM/ton (based on outdoor unit capacity), unless manufacturer states differently
Careful selection of indoor & outdoor unit combinations crucial for required airflow
Must be AHRI certified
Section 3: Airflow

## Slide 41: Equipment Set Up: Filter Selection
All filters are restrictive
If restrictive, enlarge return ducts to compensate for extra restriction
Ideally pressure drop should not be more than .1”
H20, at full flow and never more than .22” H20
Section 3: Airflow

## Slide 42: What Creates Resistance?
Friction of air moving through ducts
  The faster the air is moving (velocity), the greater
the friction
  Devices (ACCA’s word for objects placed in the
air stream) include:
    Evaporator coils
    Filters
    Registers and Grilles
Section 3: Airflow

## Slide 43: Supply Air Boot & Stack Head Fittings
Group 4
Reference Velocity = 900 FPM Reference Friction Rage = 0.08 In Wg per 100 Feet
Section 3: Airflow

## Slide 44: Plenum Fittings
Section 3: Airflow
Group 1
Reference Velocity = 900 FPM Reference Friction Rage = 0.08 In Wg per 100 Feet
Bull Head 1F | H / W | EL
 | 0.50 | 120
 | 1.0 | 85
Tapered Head 1G | H / W | EL
 | 0.50 | 35
 | 1.0 | 25

## Slide 45: Flex Duct Possibilities
6” Flex &
Sheet Metal
8” Flex & Sheet Metal
10” Flex & Sheet Metal
Section 3: Airflow
Static Pressure Loss vs. Volumetric Airflow Rate
(Maximum Stretch)

## Slide 46: Properly Installed Flex Duct
6” Sheet Metal
10” Flex
10” Sheet Metal
8” Flex
8” Sheet Metal
Section 3: Airflow
Static Pressure Loss vs. Volumetric Airflow Rate
(4% Compression)
6” Flex
**Note the change in scale**

## Slide 47: Compression Reduces Performance
Section 3: Airflow
**Note the change in scale**
Static Pressure Loss vs. Volumetric Airflow Rate
(15% Compression)
6” Flex
8” Flex
10” Flex
10” Sheet Metal
6” Sheet Metal

## Slide 48: Airflow Resistance Situation
Section 3: Airflow
48

## Slide 49: Moving Air Hates to Make Hard Turns
Section 3: Airflow
49
Photo credit: http://www.masterfile.com/stock-photography/image/600-01791391/Aerial-View-of-Freeway-Intersection-Highway-404-and-Finch-Avenue-Willowdale-Ontario-Canada

## Slide 50: Low Flow Culprits
Restrictive registers
  Open all registers; replace restrictive
registers
Restrictive air filters
  Use less restrictive air filters
Poor duct design
  Straighten ductwork
  Install turning vanes and/or more ductwork
Section 3: Airflow
50

## Slide 51: Duct Sizing: Maximize Heat Pump Performance
6 sq. in. of supply and return side duct for every 1,000 BTUs of air conditioning
Example:
  2 ton HP (24,000 BTUs) needs 144 sq. in Net Free Area (NFA) of return and supply duct
51
Section 3: Airflow

## Slide 52: Sizing Supply and Returns
Input BTUs | Sq. In. Ducts Needed (Return and Supply)
24,000 | 144
30,000 | 180
36,000 | 216
42,000 | 252
48,000 | 288
52
Heat Pumps
Section 3: Airflow

## Slide 53: Sizing Supply and Returns
Size | Sq. In.
5 | 20
6 | 28
7 | 38
8 | 50
9 | 64
10 | 79
Size | Sq. In.
12 | 113
14 | 154
16 | 201
18 | 254
20 | 314
22 | 380
53
Round Duct Sq. In. Equivalency
Section 3: Airflow

## Slide 54: Sizing Returns
General rules:
1 sq. ft. of NFA of return grille per ton
Grille NFA = 0.75 (verify with grille
manufacturer’s information)
…...Just enough for a two ton system
Grille size: 20 in x 20 in = 400 sq. in
2.78 sq. ft. x 0.75 NFA = 2.09 sq. ft. of NFA
Convert: 400 sq. in / 144 sq. in per sq. ft. = 2.78 sq. ft.
54
Section 3: Airflow

## Slide 55: Sealing the Duct System
System should be tested by PTCS Duct Sealing Technician
  Recommended, some utilities require PTCS Duct Sealing with Heat Pump installation
Use of mastic is required in the PTCS Duct Sealing specification
Section 3: Airflow
55

## Slide 56: CFM vs. Static Pressure
2000
1800
1600
1400
1200
1000
800
600
400
200
0
0
0.2
1
1.2
Airflow (CFM)
0.4 0.6 0.8
Static Pressure (IW)
PSC
ECM
Section 3: Airflow
56

## Slide 57: ure
Watts vs. Static Press
300
200
100
0
400
900
800
700
600
500
0
0.2
1
1.2
Watts
0.4 0.6 0.8
Static Pressure
PSC ECM
Section 3: Airflow
57

## Slide 58: ECM Fan Motors 2.0, 2.3m 2.5 & 3.0
Section 3: Airflow
“O” – Orange | 9 | 1 | Black – common | 
“Hum” – Black | 10 | 2 | White – “W2” | 
Heat programmed input – Brown | 11 | 3 | Black – common | 
“R” – Red | 12 | 4 |  | Red – delay programme d input
“W1” – Brown | 13 | 5 |  | White – cool programme d input
“Y2” – Yellow | 14 | 6 | Yellow – “Y1” | 
“G” – Green | 15 | 7 | Purple – adjust programmed input | 
Motor speed feedback – Yellow/Black | 16 | 8 | Black - common | 
Wiring control board requirements
58

## Slide 59: X-13 ECM Motor
24VAC
Common
Low Voltage Control Inputs
Section 3: Airflow
59

## Slide 60: Measuring Airflow
Measure External Static Pressure
Measure CFM with TrueFlow® Plate or Duct Blaster
Section 3: Airflow
Available
60
Equipment

## Slide 61: Configuring the Manometer
CONFIG
DDEEVVIICCEE
Tells manometer what measurements to display (e.g. pressure or flow)
Tells manometer what equipment is being used (TF)
Tells manometer what the equipment configuration is (plate size, #14 or #20)
CONFIG
MODE
MODE
DEVICE
61
Section 3: Airflow

## Slide 62: Measure External Static Pressure
Section 3: Airflow
Step 1
Measure Return Static Pressure (drop negative sign)
Step 2
Measure Supply Static Pressure
Step 3
Calculate External Static Pressure (ESP)
Return + Supply = ESP
62
Return | Supply | ESP
-0.280 InH2O (drop negative sign) | 0.340 InH2O | 0.280 + 0.340 = 0.620 InH2O
Example:

## Slide 63: Measure CFM with TrueFlow Plate
Normal System Operating Pressure
Same as supply static pressure with filter in place (test w/ clean filter)
Install 14 inch or 20 inch flow plate; no bypasses
TrueFlow System Operating Pressure;use same tap used for NSOP
Same as supply static with flow plate in & filter out
Calculate square root of (NSOP/TFSOP) or find using table
Ensure all air flows through the TrueFlow Plate
Find using TrueFlow Metering Plates Flow Conversion Table
Raw flow X Correction Factor = Corrected Flow
Divide corrected flow by capacity being tested
Step 1
Measure NSOP
Step 2
Install Flow Plate
Step 3
Measure TFSOP
Step 4
Calculate the Correction Factor
Step 5
Measure plate pressure
Step 6
Find Raw Flow
Step 7
Calculate Corrected Flow
Step 8
Calculate CFM/Ton
63
Section 3: Airflow

## Slide 64: Step 1: Measure NSOP (Supply Static)
Section 3: Airflow
.340
64

## Slide 65: Step 2: Install TrueFlow Plate
65
Section 3: Airflow

## Slide 66: Step 2: Install TrueFlow Plate
Section 3: Airflow
66

## Slide 67: Step 3: Measure TFSOP
Section 3: Airflow
.380
67

## Slide 68: Step 4: Calculate Correction Factor
68
Section 3: Airflow
NSOP
TFSOP
.380
.340
68

## Slide 69: Step 4: Calculate or Find Correction Factor
Calculate:
(√NSOP/TFSOP) = Correction Factor
√.340 / .380 = 0.95
OR find using table with TrueFlow Equipment
Section 3: Airflow
69

## Slide 70: Step 5: Measure Plate Pressure
Section 3: Airflow
.380
70
.210

## Slide 71: Step 6: Find Raw Flow
Section 3: Airflow
Table in Inches of H2O
TrueFlow Meter Flow Conversion Tables
0.210 In. H20 = 1112 CFM
71

## Slide 72: Steps 7 - 8: Corrected Flow to CFM/Ton
Calculate corrected flow
Calculate CFM/Ton
Raw Flow X Correction Factor = Corrected Flow
1112 CFM X 0.95 = 1056 CFM
Corrected Flow / Heat Pump Tons = CFM/Ton
1056 CFM / 3 Tons = 352 CFM/Ton
Section 3: Airflow
At least 325 CFM/ton; evidence of target must be provided if lower than 325
72

## Slide 73: Additional Correction Factor
When no return plenum is located upstream of the flow plate, use an additional 1.04 corrections factor
When testing at a remote filter grille
In manufactured homes with no
return plenum
Section 3: Airflow
Flow Plate at ceiling filter grille
Corrected Flow X 1.04 = Final Flow
73

## Slide 74: Digital True Flow
74
Section 3: Airflow

## Slide 75: Requires App and DG8 or DG1000
Section 3: Airflow
75

## Slide 76: Download True Flow HVAC Air Flow App
Section 3: Airflow
76

## Slide 77: Power On Equipment & Launch App
77
Section 3: Airflow

## Slide 78: Follow Instructions on App
Section 3: Airflow
78

## Slide 79: Input System Information & Continue Following Instructions
Section 3: Airflow
79

## Slide 80: Take Measurements & Continue Following Instructions
Section 3: Airflow
80

## Slide 81: Review Results
Section 3: Airflow
81

## Slide 82: Create a Report
82
Section 3: Airflow

## Slide 83: Increasing Measurement Accuracy
Limit obstructions within 6 inches upstream or 2 inches downstream of the flow plate
If installing spacers, install spacer directly in front of any obstructions
If flow plate is directly downstream of a 90 degree bend in the duct system, install a spacer on the inside of inside corner
Section 3: Airflow
83

## Slide 84: Estimating Airflow Using Static Pressure Measurements & Flow Tables
Also allowed by PTCS.
84

## Slide 85: Steps to Measure Airflow Using External Static Pressure Measurements
85

## Slide 86: Steps to Measure Airflow Using External Static Pressure Measurements
Measure return static pressure (downstream from the filter, 0.28 inches of water column in this example).
Measure supply plenum static pressure (0.34 inches of water column in this example).
Calculate external static pressure (return static pressure + supply static pressure; 0.28 + 0.34 = 0.62 inches of water column in this example).
86

## Slide 87: Steps to Measure Airflow Using External Static Pressure Measurements
Round the external static pressure to the nearest pressure in the manufacturer’s table (0.62 rounds to 0.60 in this example).
Find where the external static pressure and blower speed settings intersect on the manufacturer’s air flow table, 1078 CFM (shown on the table).
Confirm the CFM/ton meets PTCS specification of 325–500 CFM/ton or manufacturer specified airflow requirements. Example: This is an airflow of 359 CFM/ton if this is a 3-ton heat pump, meeting PTCS specifications.
If the airflow does not meet PTCS specifications or manufacturer specified airflow requirements, change the speed setting and restart the process at step 1.
87

## Slide 88: Measure CFM with Duct Blaster
88
If the TrueFlow cannot be used to measure airflow, use the Duct Blaster matching method.
See Duct Blaster manual here:
https://energyconservatory.com/wp- content/uploads/2014/07/Duct-Blaster-Manual- Series-B-DG700.pdf
Section 3: Airflow

## Slide 89: Exercise
‘NSOP/TFSOP Correction’ Exercise
Exercise: 10 questions
Section 3: Airflow
89

## Slide 90: Section 4 of 7: Refrigerant Charge

## Slide 91: Section 4: Refrigerant Charge
Refrigerant Charge Methods
Best Practices
Heating Mode Test
Cooling Mode Test
Piping/Electrical Penetrations

## Slide 92: Refrigerant Charge Methods
Heating
  Measure sensible temperature split & compare to chart
Cooling
  Subcooling
Alternative Methods
  Superheat
  Manufacturer’s method
Section 4: Refrigerant Charge
In communicating systems, set unit into charge/test mode.

## Slide 93: Specification Language
Temperature change across indoor coil must be at or above the minimum temperature split show in the R-410A Temperature Split Table.
  Subcooling and manufacturer approved alternative methods also acceptable
  Tables included in manual and also online
VSHP Requirement Only – Refrigerant Charge: Must be as specified in the heat pump manufacturer’s documentation. Does not need to be measured using heating or cooling methods.
Section 4: Refrigerant Charge

## Slide 94: Best Practices
Braze carefully; use nitrogen and protect TXV, etc., from heat
Evacuate system to 500 microns break with nitrogen repeat
Use new vacuum pump oil each time ($12/pint is cheap insurance)
Don’t expose R-410 to the atmosphere
Section 4: Refrigerant Charge

## Slide 95: Charging Methods
Weigh-in line set adjustment (as needed); generally
add/remove 0.6 oz. per foot for sets under/over 15’
  Add refrigerant for a longer line and remove for shorter line
  Verify charge requirements with manufacturer
Measure and compare to tables
  Outdoor temp
  Liquid/suction operating pressures
Section 4: Refrigerant Charge

## Slide 96: Heating Mode: Calculate Temp Split
Section 4: Refrigerant Charge
For Outdoor Temps Below 65oF
R-410A Minimum Expected
Temperature Split
Where ESP is measured:
Measure Supply Air Temperature Measure Return Temperature Calculate Temp Split and compare to table | Outdoor Temp oF | CFM/Ton | 
 |  | 350 | 400
 | 15 | 15.0 | 13.0
 | 17 | 15.6 | 13.6
 | 19 | 16.2 | 14.2
 | 21 | 16.8 | 14.8
 | 23 | 17.4 | 15.4
 |  | 18.0 | 16.0
Supply Air Temp – Return Air Temp = Temp Split | 25 |  | 
 | 27 | 18.6 | 16.4
90oF – 70oF = 20oF | 29 | 19.2 | 16.8
 | 31 | 19.8 | 17.2
 | 33 | 20.4 | 17.6
OAT: 320F CFM/Ton: 350
Expected Temp Split is 20oF.
Calculated Temp Split of 20oF meets target.

## Slide 97: Supply Side Ventilation
If the house has a supply side ventilation system, make sure it is closed for the temperature rise test. If it is open, the temperature test will be incorrect.
If you see this running to the outside, make sure it’s closed.
Section 4: Refrigerant Charge

## Slide 98: Cooling Mode: Calculate Sub Cooling
Section 4: Refrigerant Charge
For Outdoor Temps Above 65oF
R-410A Pressure –Temperature Chart
Liquid Saturation Temp
Liquid Line Pressure
1) Using Liquid Line Pressure, find
corresponding Liquid Saturation
Temperature
Measure Liquid Line Temperature
Calculate sub cooling
Liquid Saturation Temperature – Liquid Line Temp = Sub cooling
105.4oF – 92oF = 13.4oF
…falls within registry’s acceptable
range of 4oF to 15oF

## Slide 99: Piping/Electrical Penetrations
Section 4: Refrigerant Charge
Make sure openings in the unit cabinet and building structure are properly sealed.
Best Practice
Line set and condensate drain penetrations
Electrical penetrations

## Slide 100: Section 5 of 7: Controls

## Slide 101: Section 5: Controls
About Controls
Auxiliary (Strip) Heat Lockout
Thermostats
Other Control Requirements
Control Summary
Critical section: controls result in majority of inspection failures
101

## Slide 102: About Controls
Prioritize use of compressor to heat house
Auxiliary (strip) heat control
Compressor control
Auxiliary (strip) heat lockout set at 35oF or
below
  Controlled through thermostat; use outdoor thermistor or Wi- Fi weather station
Less chances of a problem if unit sized properly and
ducts are sealed/insulated
Section 5: Controls
102

## Slide 103: Auxiliary Heat Lockout
Controlled through thermostat or outdoor unit control board on some brands
Auxiliary (strip) heat lockout set at 35oF or below
Must use outdoor thermistor or Wi-Fi weather station
Section 5: Controls
103

## Slide 104: Dual Fuel Systems
104
Dual fuel or Hybrid systems are typically allowed depending on utility
The heat pump is the primary source of heat and switches
over to gas backup
Switchover point should be set at 35⁰F
Most of the time the systems are not wired to allow the gas furnace to engage during defrost
Keep in mind that gas heat is a lot hotter than strip heat and
can put stress on the compressor if not setup correctly
Section 5: Controls

## Slide 105: Thermostats
Wi-Fi
Communicating
Proprietary Models
Setting controls on various thermostats
Thermostat support sheets
Section 5: Controls
105

## Slide 106: Strip Heat Lockout
Follow thermostat support sheets for help with settings: https://www.bpa.gov/EE/Sectors/R esidential/Documents/Tstat_Supp ort_Sheets_ALL.pdf
QA has encountered zonal boards that overrode thermostat settings and caused jobs to fail.
Section 5: Controls
106

## Slide 107: Thermostat Test Mode
Section 5: Controls
If available, use “test mode”, but
understand what it actually does
  Use thermostat support sheets as a
reference
Also called equipment test, charge check, test compressor heat/cool, etc.
Variable-speed systems often will not heat to highest capacity at mild outdoor conditions, therefore running system in a “test” mode if often required
107

## Slide 108: Control Summary
Auxiliary (strip) heat shall be locked out above 35oF outdoor temperature
Advise consumers to use no more than a 3oF night
setback
Responsibility of the installer to ensure the
controls used meet the letter of the specs
Section 5: Controls
108

## Slide 109: Exercise
Review Thermostat support sheets
  Review example in Trainee Manual
  Found on www.bpa.gov/goto/reshvac
Section 5: Controls
109

## Slide 110: Section 6 of 7: Participation Rules & Paperwork

## Slide 111: Section 6: Participation Rules & Paperwork
111
Next Steps to Certification
Online Account
Technician Application
Entering a Job into the Mobile Registry
Quality Assurance Inspections

## Slide 112: Next Steps to Certification
Pass this training’s exam
Step 1
Create online account on ptcs.bpa.gov
Step 2
Step 3
Submit Certified Technician Application found in “How to
Participate” section on www.bpa.gov/goto/reshvac
112
Section 6: Participation Rules & Paperwork

## Slide 113: Step 2: Create Online Account Today
Go to ptcs.bpa.gov and click “Register” to create a profile.
Section 6: Participation Rules & Paperwork
Mobile view
Desktop view
Account will be activated and tech ID assigned
when all the steps are completed.
113

## Slide 114: Optional: Create Your Account In Class!
If you have a mobile device, create your account now!
Go to ptcs.bpa.gov, click on the three lined-button in the top right-hand corner, then click “Register” to create a profile.
Section 6: Participation Rules & Paperwork
114

## Slide 115: Step 3: Certified Technician Application
Find it at the end of your Trainee Manual or in the “How to Participate” section on
www.bpa.gov/goto/reshvac.
Submit photos or scans of completed & signed application by email to ResHVAC@bpa.gov or fax it to 1-877-848-4074.
Section 6: Participation Rules & Paperwork
Note: Submit this form when tech is new, receives additional training, or needs to update company info.
115

## Slide 116: Next Steps: Some Clarification
116
Technician must be PTCS Heat Pump Certified to work
through the program.
Certified technician must do the work and cannot sign
someone else’s installation forms.
Certification will follow you to any company. Must submit new
Certified Technician Application to update information.
Section 6: Participation Rules & Paperwork

## Slide 117: Beyond Certification
Install & Commission Equipment
Enter in Online Registry*
Submit Documentation to Utility
May qualify for a Quality Assurance Inspection
117
Section 6: Participation Rules & Paperwork
Get Certified
* Enter using mobile device with internet access or use the optional form for later entry

## Slide 118: Entering a Job: Mobile Registry
Section 6: Participation Rules & Paperwork
Log in to installing technician’s account at ptcs.bpa.gov and click
“Enter a Project” or click “Contractors” and select “Enter a Job”.
For a guide on entering a job online, see page 14 in your Trainee
Manual.
Mobile view
118

## Slide 119: Mobile Registry Updates
119
Online registry optimized for use on any mobile device
  Not an app you download
Save progress function to complete entered data later
  Enter job data before, during, and after installation by saving your progress
Times out after 4 hours of inactivity
Informational bubbles explaining some program components
Some limitations
  No offline entry mode. Can’t use without internet access.
  Optional forms available to record data for later entry, but not required to submit.
Section 6: Participation Rules & Paperwork

## Slide 120: Exercise: Optional Mobile Entry Practice
120
Information at the back of your trainee manual
Go to test site on a mobile device: https://ptcs.test.bpa.gov
  Only a test environment. Nothing will publish live on this site.
Sign in:
  Username:TestContractor
  Password: Ptcs1234
Click “Enter a Job” button
  Use an active physical address
  AHRI number: 7565113
  Use any data for the rest of the entry. Some suggestions:
    External Static (0.70 H2O), TrueFlow (NSOP 0.45, Plate 20, TFSOP 0.40, Plate Pressure 0.26, 3.5 ton), Refrigerant Charge (Heating mode, Outdoor Temp 57, Supply 98, Return 68)
Section 6: Participation Rules & Paperwork

## Slide 121: Troubleshooting Entry Issues
121
Contact the PTCS team if:
  Address isn’t validating
  AHRI number isn’t validating
  Need to enter in a second system
  Can’t find an entered job
  Need to edit an address or submitted data
  Need immediate review of “Pending” entry (reviewed regularly)
Section 6: Participation Rules & Paperwork

## Slide 122: Optional Air Source Heat Pump Installation Form
Section 6: Participation Rules & Paperwork
If no internet or mobile device is available or the job cannot be entered online for any reason, this form is available to record the data for later entry.
Can be found on ptcs.bpa.gov and at the end of your manual.
Note: Some participating utilities require installation form, please check with utility prior to job submission
122

## Slide 123: Notifying Utility of the Completed Job
Technician or company required to notify the utility of the completed job.
Contact customer’s utility for information on required
paperwork.
Utilities have access to the online registry and are able to review completed job details.
Section 6: Participation Rules & Paperwork
123

## Slide 124: Quality Assurance Inspections
At least 10% of all jobs are inspected for:
  Equipment Type
  External Static Pressure
  Airflow
  Refrigerant Charge
  Control Set Up
    Auxiliary (Strip) Heat Lockout
  Sizing
Section 6: Participation Rules & Paperwork
Common Inspection Failure
124

## Slide 125: Remote QA Inspections
Remote QA inspections can now be performed virtually with an inspector by using a video sharing application on a smart phone. Photo QA option is available.
After completion the PTCS staff enters the project into the PTCS registry for you!
Report to PTCS when you are commissioning your first 3 projects so we can perform a remote QA.
Contact us at resHVAC@bpa.gov to schedule your first 3 projects.
125

## Slide 126: QA Inspection Feedback & Remediation
Section 6: Participation Rules & Paperwork
Inspection feedback will be communicated to the technician and/or their company. See the “PTCS Technician Support Plan” at the end of your Trainee Manual for what to expect if a project does not pass inspection.
126

## Slide 127: Section 7 of 7: Resources

## Slide 128: Program Website
All of the following are on this website: https://ptcs.bpa.gov
  Specifications
  Requirements
  Training and Technical Resources
  Online Registry Resources
  Link to Online Marketing Portal
  Installation Forms
  Thermostat Support Sheets
Section 7: Resources
128

## Slide 129: Program Website: Technical Resources
Go to the “Heat Pump” section on
www.bpa.gov/goto/reshvac
Technical Resources for Heat Pumps include:
  Heat Pump Sizing Calculator
  Airflow Test Instructions
  Charts and Conversion Tables
  Strip Heat Cut-Out Procedure
  Variable Speed Heat Pumps Fact Sheet
  Thermostat Support Sheets
Section 7: Resources
129

## Slide 130: Spanish Materials
Now available in Spanish:
  PTCS training presentations
  Manuals
  Tests
  Forms
Contact Kyle Chase at CLEAResult: kyle.chase@clearesult.com
Section 7: Resources
130

## Slide 131: Equipment Discount
Discount now available to purchase Ducted Heat Pump testing equipment:
  12.5% discount for TrueFlow Plate
  12.5% discount for digital gauges from TEC
  8% discount for TruTech Tools
Discount form included at the end of your Trainee Manual
Submit this form to Kyle Chase at
CLEAResult: kyle.chase@clearesult.com
Section 7: Resources
131

## Slide 132: Stay Informed!
Sign up for the Quarterly Newsletter or visit the PTCS website for the latest announcements
Updated specifications
Online registry changes
Common issues in the field
Updated program requirements
New technical support resources
Tips and tricks
We guarantee we will not spam you or sell any of your information.
Section 7: Resources
Go to
https://tinyurl.com/ptcsnewsletter
or email ResHVAC@bpa.gov to sign up.
Also sign up from the “Stay Informed!”
link on the website.
132

## Slide 133: On-Demand Webinars
Section 9: Participation Rules & Paperwork
Self-led trainings available at https://clearesult.moodle.school
Prescriptive Duct Sealing Certification
Duct Sealing admin/sales training
Heat Pump admin/sales training
133

## Slide 134: NATE Continuing Education Hours
134
Email us at ResHVAC@bpa.gov
Give us your:
  Name
  Date of class
  NATE ID#
Section 7: Resources

## Slide 135: Good luck on the Exam!
Questions? Comments?
Contact the PTCS Team:
Phone: (800) 941-3867
Email: ResHVAC@bpa.gov

## Slide 136: Energy Trust of Oregon Jobs
136
For questions concerning PTCS installations for customers of Pacific Power or Portland General Electric, please call 1-866-365-3526 or email Residentialforms@energytrust.org.