## CustAutoOutages
PointOfDeliveryID | PointOfDeliveryName | OutageID | appear_in_dir_date | Cause | CauseDispatch | CauseField | ComponentID | control_center | DartActivityId | Destination | Duration | InDatetimePpt | InDatetimeUtc | IsLoadLost | IsOpsCreated | loadlost_amount | OutDatetimePpt | OutDatetimeUtc | PcbInfoFacility | PcbInfoNum_fault_operations | PcbInfoPcb_ct_pres | PcbInfoPcb_ct_prev | PcbInfopcb_lbd_fuse | PcbInfoRecloseOps | ResponsibleSystemID | ResponsibleSystemIDDispatch | ResponsibleSystemIDField | TargetInfoFacility | TargetInfoRelay_type | TargetInfoSet_num | TargetInfoTarget | Transferor | TransferTripInfoFacilityName | TransferTripInfoset_num | TransferTripInfoTarget | TransferTripInfoTransferTripType
272 | Tumble Creek: Consumers Power 24.9kV Feeder 1 | 215878 | 2020-09-11 | Unknown | Unknown |  | 4 | MCC | 1399458,1399458 |  | 3292 | 2020-09-10 12:28 | 2020-09-10 19:28 | 1 | 0 | NULL | 2020-09-08 05:36 | 2020-09-08 12:36 | NULL | NULL | NULL | NULL | NULL | NULL | BPA | BPA | BPA | NULL | NULL | NULL | NULL |  | NULL | NULL | NULL | NULL
272 | Tumble Creek: Consumers Power 24.9kV Feeder 1 | 215877 | 2020-09-09 | Unknown | Unknown |  | 4 | MCC | 1399448,1399448 |  | 0 | 2020-09-08 05:27 | 2020-09-08 12:27 | 1 | 0 | 3 | 2020-09-08 05:27 | 2020-09-08 12:27 | NULL | NULL | NULL | NULL | NULL | NULL | BPA | BPA | BPA | NULL | NULL | NULL | NULL |  | NULL | NULL | NULL | NULL

## CustPlanOutages
No customer planned outages to report

## LineAutoOutages
LineID | LineName | OutageID | appear_in_dir_date | Cause | CauseDispatch | CauseField | Component | Control_center | DartActivityId | Duration | GeneratedFlag | InDatetimePpt | InDatetimeUtc | IsOpsCreated | OutDatetimePpt | OutDatetimeUtc | ResponsibleSystem | ResponsibleSystemDispatch | ResponsibleSystemField | TreeInRightOfWay
2564 | Jones Canyon-Santiam No 1 230kV line | 215879 | NULL | Fire | Unknown | Fire | Transmission Equipment |  | 1399458,1401200 | 16837 | Generated | 2020-09-19 22:13 | 2020-09-20 05:13 | 0 | 2020-09-08 05:36 | 2020-09-08 12:36 | BPA | BPA | BPA | Unknown
2564 | Jones Canyon-Santiam No 1 230kV line | 215876 | NULL | Fire | Unknown | Fire | Transmission Equipment |  | 1399448,1399448 | 0 | Generated | 2020-09-08 05:27 | 2020-09-08 12:27 | 0 | 2020-09-08 05:27 | 2020-09-08 12:27 | BPA | BPA | BPA | Unknown
152 | Detroit-Santiam No 1 230kV line | 215851 | 2020-09-11 | Weather | Weather | Weather | Transmission Equipment | MCC | 1399392,1399470 | 3806 | from DIR file | 2020-09-10 15:45 | 2020-09-10 22:45 | 0 | 2020-09-08 00:19 | 2020-09-08 07:19 | BPA | BPA | BPA | Unknown
145 | John Day-Marion No 1 500kV line | 215901 | 2020-09-10 | Fire | Smoke | Fire | Transmission Equipment | DCC | 1399668,1399668 | 1052 | from DIR file | 2020-09-09 13:45 | 2020-09-09 20:45 | 0 | 2020-09-08 20:13 | 2020-09-09 03:13 | BPA | BPA | BPA | Unknown
145 | John Day-Marion No 1 500kV line | 215900 | 2020-09-09 | Fire | Smoke | Fire | Transmission Equipment | DCC | 1399670,1399670 | 0 | from DIR file | 2020-09-08 20:12 | 2020-09-09 03:12 | 0 | 2020-09-08 20:12 | 2020-09-09 03:12 | BPA | BPA | BPA | Unknown
145 | John Day-Marion No 1 500kV line | 215899 | 2020-09-09 | Smoke | Smoke | Smoke | Transmission Equipment | DCC | 1399666,1399666 | 8 | from DIR file | 2020-09-08 20:10 | 2020-09-09 03:10 | 0 | 2020-09-08 20:02 | 2020-09-09 03:02 | BPA | BPA | BPA | Unknown
145 | John Day-Marion No 1 500kV line | 215859 | 2020-09-09 | Fire | Fire | Fire | Transmission Equipment | DCC | 1399416,1399416 | 494 | from DIR file | 2020-09-08 10:06 | 2020-09-08 17:06 | 0 | 2020-09-08 01:52 | 2020-09-08 08:52 | BPA | BPA | BPA | Unknown
485 | Big Cliff-Detroit PH No 1&2 13.8kV line | 215928 | 2020-09-11 | Forced (Configuration) | Forced (Configuration) |  |  | MCC | 1400016,1400016 | 3806 | from DIR file | 2020-09-10 15:45 | 2020-09-10 22:45 | 0 | 2020-09-08 00:19 | 2020-09-08 07:19 | BPA | BPA |  | Unknown
124 | Buckley-Marion No 1 500kV line | 215854 | 2020-09-09 | Fire | Fire | Fire | Transmission Equipment | DCC | 1399416,1399416 | 789 | from DIR file | 2020-09-08 15:01 | 2020-09-08 22:01 | 0 | 2020-09-08 01:52 | 2020-09-08 08:52 | BPA | BPA | BPA | Unknown
32 | Ashe-Marion No 2 500kV line | 215896 | 2020-09-09 | Smoke | Smoke | Smoke | Transmission Equipment | DCC | 1399662,1399662 | 0 | from DIR file | 2020-09-08 19:47 | 2020-09-09 02:47 | 0 | 2020-09-08 19:47 | 2020-09-09 02:47 | BPA | BPA | BPA | Unknown
32 | Ashe-Marion No 2 500kV line | 215853 | 2020-09-09 | Fire | Fire | Fire | Transmission Equipment | DCC | 1399416,1399416 | 785 | from DIR file | 2020-09-08 14:57 | 2020-09-08 21:57 | 0 | 2020-09-08 01:52 | 2020-09-08 08:52 | BPA | BPA | BPA | Unknown

## LinePlanOutages
No line planned outages to report

## Comments
OutageID | Comment | CommentDate | CommentType | FacilityName
215851 | A-320 open at Detroit Sub (outage 215929). Santiam KDs detect BC fault and trip inst. Santiam DFR: Ib ~= Ic ~= 6200 Arms. | 2020-11-05 16:03 | System Protection and Control | Detroit Substation
215851 | The Detroit-Santiam #1 230KV Line tripped by relay action during wind/fire storm. Reclosing is normally cut-out at both terminals. line was patrolled by TLM, after finding nothing in line the line was reenergized successfully by MCC. This Line outage forced out both Detroit Power House 230KV Lines #1 & #2. | 2020-09-14 07:33 | Substation Operations | Detroit Substation
215851 | No JM annunciator targets??? | 2020-09-09 19:34 | Substation Operations | Santiam Substation
215853 | Evolving fault: BG fault >> hybrid trip start, B phase open >> CG fault (while hybrid trip timer was timing) >> 3-phase trip >> improper reclose >> ABC fault >> SOTF trip/lockout. Additional Trouble: the relay should not have reclosed after the 3-phase trip. SPC Branch investigated, correction made to reclose logic. | 2020-10-07 17:12 | System Protection and Control | Marion Substation
215853 | Ashe Marion #2 500kV line tripped to lockout. Fire and smoke in area outside of Marion, affecting numerous BPA lines. Terminal inspect of Ashe HV equipment including PCBs 4937 & 4940 found no issues. SEMM B phase evolving to a 3 phase fault FLAR 14.88 mi from Marion. | 2020-09-09 13:26 | Substation Operations | Ashe Substation
215853 | Marion terminal equipment inspected. | 2020-09-08 20:05 | Substation Operations | Marion Substation
215854 | Marion terminal equipment inspected. | 2020-09-08 20:24 | Substation Operations | Marion Substation
215854 | On 09/08/2020 at about 01:52 a C phase to A phase fault was detected on the Buckley – Marion line. The SEL-421 relay at Buckley substation detected the fault to be about 90 miles away from Buckley substation. Since the line is about 99.33 miles long that would place the fault about 90.6% of the way down the line from Buckley which places the fault outside of the zone 1 but still inside the zone 2 protection zone. Buckley sent a permissive trip signal and received a permissive and direct trip signal which caused the relays at Buckley to trip off the line at which point Buckley also sent a direct trip signal back. The PCBs appear to have opened in three cycles or less after receiving the trip signal. Since it was a multi-phase fault the breakers were tripped three pole. From the Buckley relays it appears as though the Marion side attempted to reclose but was unsuccessful so a reclose block signal was sent to the Buckley relays from the Marion Relays. | 2020-09-30 14:06 | System Protection and Control | Buckley Substation
215859 | Evolving fault: AG fault >> hybrid trip start, A-phase open >> BC fault >> 3ph trip | 2020-09-24 18:13 | System Protection and Control | Marion Substation
215859 | Marion terminal equipment inspected. | 2020-09-08 20:39 | Substation Operations | Marion Substation
215876 | Appeared to be a successful reclose. equipment inspected. | 2020-09-09 19:28 | Substation Operations | Santiam Substation
215876 | One operation with successful reclose. All terminal equipment inspected and appears normal. | 2020-09-10 12:23 | Substation Operations | Jones Canyon Substation
215879 | Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team. | 2020-11-25 10:06 | Technical Operations | NULL
215879 | Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. | 2020-09-10 12:20 | Substation Operations | Jones Canyon Substation
215879 | Multi phase fault with unsuccessful reclose. Equipment inspected. | 2020-09-09 19:32 | Substation Operations | Santiam Substation
215879 | Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. | 2020-11-05 18:27 | System Protection and Control | Santiam Substation
215896 | Ashe - Marion #2 500kV line trip and reclosed. B phase to grd fault. Fire and smoke in the area outside Marion affecting numerous BPA lines. Terminal inspection of affected high voltage equipment at Ashe complete with no issues found. PCBs 4937 and 4940 at Ashe. | 2020-09-09 13:11 | Substation Operations | Ashe Substation
215896 | FLAR SHOWS 21.7MILES FROM MARION, SEMM 'B' PHASE. | 2020-09-09 05:20 | System Dispatch | NULL
215896 | B-phase to ground fault with successful reclose. Marion terminal equipment inspected. | 2020-09-09 19:42 | Substation Operations | Marion Substation
215899 | Evolving fault: BG fault >> hybrid trip >> reclose >> AB fault >> 3ph trip | 2020-09-24 18:00 | System Protection and Control | Marion Substation
215899 | This fault was masked , see ID 215901 | 2020-09-09 19:44 | Substation Operations | Marion Substation
215899 | Spc(JDAY) Type of fault changed from 1 Line to Ground to 3 Phase per the Outage Review Team. | 2020-12-13 16:35 | Technical Operations | NULL
215900 | OPERATOR REPORTS PHASE TO PHASE, 22 MILES FROM MARION. | 2020-09-09 05:20 | System Dispatch | NULL
215900 | This fault was masked by future fault, see ID 215901 | 2020-09-09 19:45 | Substation Operations | Marion Substation
215901 | BG fault >> hybrid trip >> reclose (held ~7s) >> BG fault >> 3ph trip (TOPD = 900cyc) | 2020-09-24 18:07 | System Protection and Control | Marion Substation
215901 | OPERATOR REPORTS PHASE TO PHASE, 22 MILES FROM MARION. | 2020-09-09 05:20 | System Dispatch | NULL
215901 | Set 2 never produced any fault location data, while I was gathering data. | 2020-09-09 19:53 | Substation Operations | Marion Substation
215901 | PCB 4170 TRIPPED, RECLOSED THEN LOCKED OUT PCB 4167 TRIPPED, RECL RELAY IS NORMALLY C/O | 2020-10-20 09:51 | Substation Operations | John Day Substation

## SPCTroubleReports
OutageID | FacilityName | AdditionalTrouble | Cause | Component | CorrectiveActionDatetimePpt | CorrectiveActionDescription | FailedToOperate | fault_loc | FaultClearing | FinalAnalysisCompleteDatetime | FuseOperation | IsAPhase | IsBPhase | IsCPhase | IsGround | MinimumAnalysisDatetime | num_of_faults | OperatedForNoFault | OperatedForOutsideFault | out_millisecond | OutDatetimePpt | PowerSwingDatetime | PowerSwingDescription | ProblemDescription | ProtectionSystemPart | RecloseSpc | ReferenceDocument | RelayPrimary | RelaySecondary | report_by | ResponsibleSystem | SystemControl | TransferTrip | TypeOfFault | UnsuccessfulReclose | Update_datePpt | UserName
215851 | Detroit Substation |  |  |  | NULL |  | 0 |  |  | 2020-09-15 15:02 |  | 0 | 0 | 0 | 0 | 2020-09-15 15:02 | 0 | 0 | 0 | 191 | 2020-09-08 00:18 | NULL | No | [6 empty] | Murphy, Sean | [5 empty] | 2020-11-05 16:23 | SDM1560
215851 | Santiam Substation |  | Weather | Transmission Equipment | NULL |  | 0 | ASPEN: 5.2 miles | Instantaneous | 2020-09-15 13:04 |  | 0 | 1 | 1 | 0 | 2020-09-15 13:04 | 1 | 0 | 0 | 191 | 2020-09-08 00:18 | NULL | No |  |  | Cut Out or None |  | Proper 3 Phase |  | Murphy, Sean | BPA | Not Applicable | None | Phase to Phase |  | 2020-11-05 16:24 | SDM1560
215853 | Ashe Substation |  | Fire | Conductor/Hardware | NULL |  | 0 | 209.13 MILES (FLAR) | Instantaneous | 2020-09-17 13:12 |  | 0 | 1 | 0 | 1 | 2020-09-17 13:12 | 2 | 0 | 0 | 229 | 2020-09-08 01:52 | NULL | No |  |  | Unsuccessful |  | Proper Hybrid |  | Atkinson, Richard | BPA | Proper | Proper | Evolving | Permanent Fault | 2020-09-17 13:12 | RWA4045
215853 | Marion Substation | Additional Trouble |  | Transmission Equipment | NULL |  | 0 | FLAR (line method): 203.5 miles | Instantaneous | 2020-09-25 17:24 |  | 1 | 1 | 1 | 1 | 2020-09-25 17:24 | 3 | 0 | 0 | 32 | 2020-09-08 01:52 | NULL | No |  |  | Unsuccessful |  | Proper 3 Phase |  | Murphy, Sean | BPA | Proper | Proper | Evolving | Permanent Fault | 2020-09-25 17:25 | SDM1560
215854 | Marion Substation |  |  | Transmission Equipment | NULL |  | 0 | FLAR (remote method): 84.45 miles | Instantaneous | 2020-09-18 16:45 |  | 1 | 0 | 1 | 0 | 2020-09-18 16:45 | 1 | 0 | 0 | 231 | 2020-09-08 01:52 | NULL | No |  |  | Failed to Reclose |  | Proper 3 Phase |  | Murphy, Sean | BPA | Proper | Proper | Phase to Phase | Reclose Blocked: Proper | 2020-09-18 16:45 | SDM1560
215854 | Buckley Substation |  | Fire | Transmission Equipment | NULL |  | 0 | 90 miles from Buckley substation per the SEL-421 at Buckley substation. | Instantaneous | 2020-09-30 14:06 |  | 1 | 0 | 1 | 0 | 2020-09-30 14:06 | 1 | 0 | 0 | 0 | 2020-09-08 01:52 | NULL | No |  |  | Unsuccessful |  | Proper 3 Phase |  | Glenn Smart | BPA |  | Proper | Phase to Phase | Permanent Fault | 2020-09-30 14:06 | GAS5766
215859 | Marion Substation |  | Fire | Transmission Equipment | NULL |  | 0 | FLAR (remote method): 111.96 miles | Instantaneous | 2020-09-08 15:33 |  | 1 | 1 | 1 | 1 | 2020-09-08 15:33 | 1 | 0 | 0 | 13 | 2020-09-08 01:52 | NULL | No |  |  | Failed to Reclose |  | Proper 3 Phase |  | Murphy, Sean | BPA | Proper | Proper | Evolving | Reclose Blocked: Proper | 2020-09-24 18:12 | SDM1560
215859 | John Day Substation |  | Fire | Transmission Equipment | NULL |  | 0 | 112 miles (FLAR) | Instantaneous | 2020-10-05 22:14 |  | 1 | 0 | 0 | 1 | 2020-10-05 22:14 | 1 | 0 | 0 | 151 | 2020-09-08 01:52 | NULL | No |  |  | Successful |  | Proper Hybrid |  | Short, Lucas | BPA | Proper | Proper | 1 Line to Ground |  | 2020-10-05 22:14 | LMS9940
215876 | Santiam Substation |  |  | Transmission Equipment | NULL |  | 0 | FLAR: 136.1 miles | Instantaneous | 2020-09-18 13:01 |  | 1 | 1 | 0 | 0 | 2020-09-18 13:01 | 1 | 0 | 0 | 33 | 2020-09-08 05:27 | NULL | No |  |  | Successful |  | Proper 3 Phase |  | Murphy, Sean | BPA | Proper | Proper | Phase to Phase |  | 2020-11-05 16:51 | SDM1560
215876 | Jones Canyon Substation |  | Fire | Transmission Equipment | NULL |  | 0 | SEL 321: 140 miles from Jones Canyon | Instantaneous | 2020-09-30 17:04 |  | 1 | 1 | 0 | 0 | 2020-09-30 17:04 | 1 | 0 | 0 | 0 | 2020-09-08 05:27 | NULL | No |  |  | Successful |  | Proper 3 Phase |  | S. Woodside | BPA | Proper | Proper | 2 Line to Ground |  | 2020-09-30 17:04 | SLW2941
215879 | Santiam Substation |  | Fire | Transmission Equipment | NULL |  | 0 | FLAR: 136.7 miles | Instantaneous | 2020-09-18 13:22 |  | 1 | 1 | 1 | 0 | 2020-09-18 13:22 | 2 | 0 | 0 | 90 | 2020-09-08 05:36 | NULL | No |  |  | Failed to Reclose |  | Proper 3 Phase |  | Murphy, Sean | BPA | Proper | Proper | Evolving | Reclose Blocked: Proper | 2020-11-25 10:05 | RME5820
215879 | Jones Canyon Substation |  | Fire | Transmission Equipment | NULL |  | 0 | SEL 321: 136 miles from Jones Canyon | Instantaneous | 2020-09-30 17:07 |  | 1 | 1 | 1 | 1 | 2020-09-30 17:07 | 2 | 0 | 0 | 0 | 2020-09-08 05:36 | NULL | No |  |  | Partly Successful |  | Proper 3 Phase |  | S. Woodside | BPA | Proper | Proper | 3 Phase | Temporary Fault | 2020-09-30 17:07 | SLW2941
215896 | Ashe Substation |  | Smoke | Conductor/Hardware | NULL |  | 0 | 202 MILES (FLAR) | Instantaneous | 2020-09-17 15:14 |  | 0 | 1 | 0 | 1 | 2020-09-17 15:14 | 1 | 0 | 0 | 0 | 2020-09-08 19:47 | NULL | No |  |  | Successful |  | Proper Hybrid |  | Atkinson, Richard | BPA | Proper | Proper | 1 Line to Ground |  | 2020-09-17 15:14 | RWA4045
215896 | Marion Substation |  | Smoke | Transmission Equipment | NULL |  | 0 | FLAR (remote method): 202.3 miles | Instantaneous | 2020-09-18 11:24 |  | 0 | 1 | 0 | 1 | 2020-09-18 11:24 | 1 | 0 | 0 | 169 | 2020-09-08 19:47 | NULL | No |  |  | Successful |  | Proper Hybrid |  | Murphy, Sean | BPA | Proper | Proper | 1 Line to Ground |  | 2020-09-25 12:38 | SDM1560
215899 | Marion Substation |  |  | Transmission Equipment | NULL |  | 0 | SEL-321: 111.8 miles | Instantaneous | 2020-09-15 10:27 |  | 1 | 1 | 0 | 1 | 2020-09-15 10:27 | 2 | 0 | 0 | 109 | 2020-09-08 20:02 | NULL | No |  |  | Unsuccessful |  | Proper Hybrid |  | Murphy, Sean | BPA | Proper | Proper | Evolving | Permanent Fault | 2020-09-24 17:28 | SDM1560
215899 | John Day Substation |  | Smoke | Transmission Equipment | NULL |  | 0 | 130.1 miles (SEL) | Instantaneous | 2020-10-05 22:29 |  | 0 | 1 | 0 | 1 | 2020-10-05 22:29 | 2 | 0 | 0 | 0 | 2020-09-08 20:02 | NULL | No |  |  | Unsuccessful |  | Proper Hybrid |  | Short, Lucas | BPA | Proper | Proper | 3 Phase | Permanent Fault | 2020-12-13 16:34 | RME5820
215900 | Marion Substation |  |  | Transmission Equipment | NULL |  | 0 | FLAR (line method): 104.6 miles | Instantaneous | 2020-09-15 11:07 |  | 0 | 1 | 0 | 1 | 2020-09-15 11:07 | 1 | 0 | 0 | 90 | 2020-09-08 20:12 | NULL | No |  |  | Successful |  | Proper Hybrid |  | Murphy, Sean | BPA | Proper | Proper | 1 Line to Ground |  | 2020-09-24 17:37 | SDM1560
215900 | John Day Substation |  | Smoke | Transmission Equipment | NULL |  | 0 | 119.6 miles (SEL) | Instantaneous | 2020-10-05 22:32 |  | 0 | 1 | 0 | 1 | 2020-10-05 22:32 | 1 | 0 | 0 | 0 | 2020-09-08 20:12 | NULL | No |  |  | Successful |  | Proper Hybrid |  | Short, Lucas | BPA | Not Applicable | Proper | 1 Line to Ground |  | 2020-10-05 22:32 | LMS9940
215901 | Marion Substation |  |  | Transmission Equipment | NULL |  | 0 | FLAR (remote method): 104.9 miles | Instantaneous | 2020-09-18 13:37 |  | 0 | 1 | 0 | 1 | 2020-09-18 13:37 | 2 | 0 | 0 | 211 | 2020-09-08 20:13 | NULL | No |  |  | Unsuccessful |  | Proper Hybrid |  | Murphy, Sean | BPA | Proper | Proper | 1 Line to Ground | Permanent Fault | 2020-09-24 17:54 | SDM1560
215901 | John Day Substation |  | Smoke | Transmission Equipment | NULL |  | 0 | 118.5 miles (SEL) | Instantaneous | 2020-10-05 22:35 |  | 0 | 1 | 0 | 1 | 2020-10-05 22:35 | 2 | 0 | 0 | 0 | 2020-09-08 20:13 | NULL | No |  |  | Unsuccessful |  | Proper Hybrid |  | Short, Lucas | BPA | Proper | Proper | 1 Line to Ground | Permanent Fault | 2020-10-05 22:35 | LMS9940

## SubOpsTroubleReports
OutageID | FacilityName | Cause | Component | fault_loc | IsLoadLost | loadlost_amount | DfrOscOperatedID | report_by | ResponsibleSystem | temperature | update_date | UserName | weather
215851 | Detroit Substation | Weather | Conductor/Hardware |  | 0 | NULL | 1 | F Black |  |  | 2020-09-14 07:33 | FBB3889
215851 | Santiam Substation |  |  |  | 0 | NULL | 1 | F Black |  |  | 2020-09-09 19:34 | FBB3889
215853 | Ashe Substation | Fire | Conductor/Hardware | ~220.4/224.4 mi from Ashe | 0 | NULL | 2 | Mike Pilbeam | BPA | 40s | 2020-09-09 13:20 | GTL6445 | Hazy, smokey
215853 | Marion Substation |  | Conductor/Hardware | 19.6 mi. | 0 | NULL | 1 | F Black |  |  | 2020-09-08 20:04 | FBB3889
215854 | Marion Substation |  | Conductor/Hardware |  | 0 | NULL | 1 | F Black |  |  | 2020-09-08 20:24 | FBB3889
215854 | Buckley Substation | Fire | Transmission Equipment | 90 miles | 0 | NULL | 2 | Mark Fuller |  |  | 2020-09-08 11:05 | MJF6859
215859 | Marion Substation |  | Conductor/Hardware |  | 0 | NULL | 1 | F Black |  |  | 2020-09-08 20:39 | FBB3889
215859 | John Day Substation | Fire | Transmission Equipment | 128 | 0 | NULL | 2 | M DUCKWALL | BPA | UNKNOWN | 2020-09-21 12:30 | MAT7199 | UNKNOWN
215876 | Santiam Substation |  | Conductor/Hardware |  | 0 | NULL | 2 | F Black |  |  | 2020-09-09 19:27 | FBB3889
215876 | Jones Canyon Substation |  | Conductor/Hardware | 140 | 0 | NULL | 1 | Eric Tolon | BPA |  | 2020-09-10 12:23 | EGT5176
215877 | Tumble Creek Substation |  | Conductor/Hardware | 140 | 0 | NULL | 1 | Eric Tolon | BPA |  | 2020-09-10 12:23 | EGT5176
215878 | Tumble Creek Substation |  | Conductor/Hardware | 143 | 0 | NULL | 1 | Eric Tolon | BPA |  | 2020-09-10 12:20 | EGT5176
215879 | Santiam Substation |  | Conductor/Hardware |  | 0 | NULL | 1 | F Black |  |  | 2020-09-09 19:32 | FBB3889
215879 | Jones Canyon Substation |  | Conductor/Hardware | 143 | 0 | NULL | 1 | Eric Tolon | BPA |  | 2020-09-10 12:20 | EGT5176
215896 | Ashe Substation | Smoke | Conductor/Hardware | ~229.9/229.8 miles from Ashe by Relay | 0 | NULL | 2 | Garth Lien | BPA | 80s | 2020-09-09 13:15 | GTL6445 | Hazy / Smokey
215896 | Marion Substation |  | Conductor/Hardware | 22 mi. | 0 | NULL | 2 | F Black | BPA |  | 2020-09-09 19:42 | FBB3889
215899 | Marion Substation |  | Conductor/Hardware |  | 0 | NULL | 1 | F Black |  |  | 2020-09-09 19:43 | FBB3889
215899 | John Day Substation | Fire | Transmission Equipment | 130.1 | 0 | NULL | 2 | M DUCKWALL | BPA | UNKNOWN | 2020-10-20 10:00 | MAT7199 | UNKNOWN
215900 | Marion Substation |  | Conductor/Hardware |  | 0 | NULL | 2 | F Black | BPA |  | 2020-09-09 19:44 | FBB3889
215900 | John Day Substation | Fire | Transmission Equipment | 119.6 | 0 | NULL | 2 | M. DUCKWALL | BPA | UNKNOWN | 2020-10-20 09:55 | MAT7199 | UNKNOWN
215901 | Marion Substation | Smoke | Conductor/Hardware | 15.71 - 21.71 miles | 0 | NULL | 2 | F Black | BPA |  | 2020-09-09 19:53 | FBB3889
215901 | John Day Substation | Fire | Transmission Equipment | 118 | 0 | NULL | 2 | M DUCKWALL | BPA | UNKNOWN | 2020-10-20 09:51 | MAT7199 | UNKNOWN

## SubOpsTargetInfo
OutageID | FacilityDescription | set_num | relay_type | target
215851 | Detroit Substation | 1 | SEL-311L | TRIP / COMM
215851 | Detroit Substation | 2 | SEL-311L | TRIP / COMM
215851 | Santiam Substation | 1 | KD-10 | Zone 1
215853 | Ashe Substation | 1 | SEL 321 | COM, Z2, C, G, TRIP, 220.4mi
215853 | Ashe Substation | 2 | SEL 321 | COM, Z2, C, G, TRIP, 224.4mi
215853 | Marion Substation | 1 | SEL-321 | SOTF / Z4 / A / C (q= BG +19.53 mi.)
215853 | Marion Substation | 2 | SEL-321 | SOTF / Z4 / A / C (q= BG +19.86 mi.)
215854 | Marion Substation | 1 | SEL-421 | TRIP / Z1 / A / C / 50 (q= CA T +14.61 mi.)
215854 | Marion Substation | 2 | RED-670 | TRIP (q= L3_L1 Z3 p.u.)
215854 | Buckley Substation | 1 | SEL 421 | T, Comm, Z2, Z4, A phase to C phase, 50.
215854 | Buckley Substation | 2 | RED 670 | Pickup, T, a phase to c phase.
215859 | Marion Substation | 1 | SEL-321 | INST / Z1 / A / C ((q= AG +15.64mi.)
215859 | Marion Substation | 2 | REL-531 | START / TRIP (q= L1_N +15.4 mi.)
215859 | John Day Substation
215859 | John Day Substation | 1 | SEL 321 | A, G, COMM, Z2
215859 | John Day Substation | 2 | REL 531 | L-G, TRIP & START
215876 | Jones Canyon Substation | 1 | SEL 321 | INST, ZONE 2, B, C, (HMI: AB, 140.8)
215876 | Jones Canyon Substation | 2 | SEL 321 | INST, ZONE 2, B, C, (HMI: AB, 140.5)
215876 | Santiam Substation | 1 | SEL-321 | INST / Z1 / B / C (q= AB +18.41mi.)
215876 | Santiam Substation | 2 | SEL-321 | INST / Z1 / B / C (q= AB T +18.69mi.)
215876 | Santiam Substation | 1 | BE1-50BF | INST (retrip)
215879 | Santiam Substation | 1 | SEL-321 | INST / Z1 / B / C (q= ABC +16.84 mi. & BC +16.9 mi.)
215879 | Santiam Substation | 2 | SEL-321 | INST / Z1 / B / C (q= ABC +16.91 mi. & BC +16.73 mi.)
215879 | Santiam Substation | 1 | BE1-50BF | INST (retrip)
215879 | Jones Canyon Substation | 1 | SEL 321 | INST, ZONE 2, B, C (HMI: ABC, 136.8, BC, 143.1
215879 | Jones Canyon Substation | 2 | SEL 321 | INST, ZONE 2, B, C (HMI: ABC, 136.8, BC, 143.2)
215896 | Ashe Substation | 1 | SEL-321 | BG +229.9mi
215896 | Ashe Substation | 2 | SEL-321 | BG +229.8mi
215896 | Marion Substation | 1 | SEL-321 | INST / Z1 / B / G (q= BG +21.6mi.)
215896 | Marion Substation | 2 | SEL-321 | INST / Z1 / B / G (q= BG T +22.17mi.)
215899 | John Day Substation | 1 | SEL 321 | COMM, Z2, EN, B, G
215900 | John Day Substation | 1 | SEL 321 | COMM, Z2, EN, B,G
215901 | John Day Substation | 1 | SEL 321 | COMM, Z2, EN, B,G
215901 | Marion Substation | 1 | SEL-321 | INST / SOTF / Z1 / A / B (q= AB +15.71, 21.71)
215901 | Marion Substation | 2 | REL-531 | START/TRIP

## SubOpsPcbInfo
OutageID | FacilityDescription | pcb_lbd_fuse | RecloseOpsDescription | pcb_ct_prev | pcb_ct_pres | num_fault_operations
215851 | Detroit Substation | A-320 | Disabled | 568 | 569 | 1
215851 | Santiam Substation | A-536 | Disabled | 440 | 441 | 1
215853 | Ashe Substation | 4940 A | Enabled | 987 | 988 | 1
215853 | Ashe Substation | 4940 B | Enabled | 992 | 993 | 1
215853 | Ashe Substation | 4940 C | Enabled | 995 | 996 | 1
215853 | Ashe Substation | 4937 A | Enabled | 852 | 853 | 1
215853 | Ashe Substation | 4937 B | Enabled | 857 | 858 | 1
215853 | Ashe Substation | 4937 C | Enabled | 859 | 860 | 1
215853 | Marion Substation | 4380 (A-phase) | Enabled | 213 | 215 | 2
215853 | Marion Substation | 4377 (A-phase) | Disabled | 803 | 804 | 1
215854 | Marion Substation | 4389 (A-phase) | Enabled | 396 | 397 | 1
215854 | Marion Substation | 4386 (A-phase) | Enabled | 374 | 375 | 1
215854 | Buckley Substation | 4964 | Enabled | 1135 | 1136 | 1
215854 | Buckley Substation | 4967 | Enabled | 1507 | 1508 | 1
215859 | John Day Substation | 4170-A | Enabled | 2414 | 2415 | 1
215859 | John Day Substation | 4167-A | Disabled | 843 | 844 | 1
215859 | Marion Substation | 4371 (A-phase) | Enabled | 2094 | 2095 | 1
215859 | Marion Substation | 4368 (A-phase) | Disabled | 19 | 20 | 1
215876 | Santiam Substation | A-528 | Enabled | 280 | 281 | 1
215876 | Jones Canyon Substation | A-1682 | Enabled | 242 | 243 | 1
215876 | Jones Canyon Substation | A-1685 | Enabled | 258 | 259 | 1
215879 | Jones Canyon Substation | A-1682 | Enabled | 243 | 245 | 2
215879 | Jones Canyon Substation | A-1685 | Enabled | 259 | 261 | 2
215879 | Santiam Substation | A-528 | Enabled | 281 | 283 | 2
215896 | Ashe Substation | 4940 A | Enabled | 988 | 989 | 1
215896 | Ashe Substation | 4940 B | Enabled | 993 | 994 | 1
215896 | Ashe Substation | 4940 C | Enabled | 996 | 997 | 1
215896 | Ashe Substation | 4937 A | Enabled | 853 | 854 | 1
215896 | Ashe Substation | 4937 B | Enabled | 858 | 859 | 1
215896 | Ashe Substation | 4937 C | Enabled | 859 | 860 | 1
215896 | Marion Substation | 4380 (B-phase) | Enabled | 215 | 216 | 1
215896 | Marion Substation | 4377 (B-phase) | Disabled | 799 | 800 | 1
215899 | John Day Substation | 4167B | Disabled | 4814 | 4815 | 1
215899 | John Day Substation | 4170B | Enabled | 843 | 844 | 1
215900 | John Day Substation | 4167-B | Disabled | 2415 | 2416 | 1
215900 | John Day Substation | 4170B | Enabled | 845 | 846 | 1
215901 | John Day Substation | 4167 B | Disabled | 2417 | 2418 | 1
215901 | John Day Substation | 4170-B | Enabled | 845 | 847 | 2
215901 | Marion Substation | 4371 (A-phase) | Enabled | 2096 | 2100 | 4
215901 | Marion Substation | 4368 (A-phase) | Disabled | 18 | 20 | 2

## SubOpsTransTripInfo
OutageID | FacilityDescription | set_num | Target | TransferTripDescription
215853 | Ashe Substation | 1 & 2 | Mirror bit transfer trip, no data availabe to operations. | Mirror Bit Transfer Trip
215854 | Buckley Substation | 1 | DTR | Mirror Bit Transfer Trip
215896 | Ashe Substation | 1&2 | Mirror Bit Transfer Trip - no data available to operations | Mirror Bit Transfer Trip

## Notes
Outages from OARS for the period 2020_09_05 00:00 through 2020_09_08 23:59, inclusive, for the following equipment (equipment list from 6/2/2021 14:00-15:00 Stephen Gallman litigation hold meeting):
Ashe-Marion No 2 500kV line
Big Cliff-Detroit PH No 1&2 13.8kV line
Buckley-Marion No 1 500kV line
Detroit-Santiam No 1 230kV line
John Day-Marion No 1 500kV line
Jones Canyon-Santiam No 1 230kV line
Tumble Creek-Hall Ridge No 1 2.4kV line | BPA does not record outages for this line
Tumble Creek: Consumers Power 24.9kV Feeder 1 | Point of Delivery added because of its association with the Jones Canyon-Santiam No 1 230kV line