## Report
Line and segments, Planned, Automatic from 9/5/2020 00:00 to 9/8/2020 23:59 for Transmission Lines Ashe-Marion No 2 500kV line, Big Cliff-Detroit PH No 1&2 13.8kV line, Buckley-Marion No 1 500kV line, Detroit-Santiam No 1 230kV line, John Day-Marion No 1 500kV line, Jones Canyon-Santiam No 1 230kV line, Ordered by out_datetime
Customer , Planned, Automatic from 9/5/2020 00:00 to 9/8/2020 23:59, Tumble Creek: Consumers Power 24.9kV Feeder 1 Ordered by out_datetime
Outage ID | Tred ID | Customer Name | Transformer/Line/POD Name | Type | Gen Flag | kV | Ops Spc HQ | O&M District | Trans Owner NERC TADS | Length (Mi) | OutDatetime (Pacific Prevailing Time) | InDatetime (Pacific Prevailing Time) | Dur Mins | Auto Plan | Cause | Responsible System | Component | Weather | Temperature (F) | Fault Location | Dfr/Osc Operated | Comments
107973 | 32 |  | Ashe-Marion No 2 500kV line | L | T | 500 | ASH CHE | TRI TDA RED SAL | BPAT | 224.01 | 1988-01-01 11:00 |  | Still Out | Plan | Normally Out | BPA | [5 empty] | [TOps980305]: Added tap outage 3/5/98. This tap is normally open and is out. ALH
107973 | 1092 |  | Slatt tap to Ashe-Marion No 2 500kV line | T |  | 500 | ASH CHE | TRI | BPAT | 0.1 | 1988-01-01 11:00 |  | Still Out | Plan | Normally Out | BPA | [5 empty] | [TOps980305]: Added tap outage 3/5/98. This tap is normally open and is out. ALH
215928 | 485 |  | Big Cliff-Detroit PH No 1&2 13.8kV line | L |  | 13.8 | CHE | SAL | BPAT | 5.66 | 2020-09-08 00:19 | 2020-09-10 15:45 | 3806 | Auto | Forced (Configuration) | BPA
215851 | 152 |  | Detroit-Santiam No 1 230kV line | L |  | 230 | CHE | SAL | BPAT | 22.8 | 2020-09-08 00:19 | 2020-09-10 15:45 | 3806 | Auto | Weather | BPA | Transmission Equipment | [DETR200914]: [SANT200909]: | [DETR200914]: [SANT200909]: | [DETR200914]: [SANT200909]: | [DETR200914]: [SANT200909]: | [Ops(SANT)200909]: No JM annunciator targets??? [Ops(DETR)200914]: The Detroit-Santiam #1 230KV Line tripped by relay action during wind/fire storm. Reclosing is normally cut-out at both terminals. line was patrolled by TLM, after finding nothing in line the line was reenergized successfully by MCC. This Line outage forced out both Detroit Power House 230KV Lines #1 & #2. [Spc(CHHQ)201105]: A-320 open at Detroit Sub (outage 215929). Santiam KDs detect BC fault and trip inst. Santiam DFR: Ib ~= Ic ~= 6200 Arms.
215853 | 32 |  | Ashe-Marion No 2 500kV line | L |  | 500 | ASH CHE | TRI TDA RED SAL | BPAT | 224.01 | 2020-09-08 01:52 | 2020-09-08 14:57 | 785 | Auto | Fire | BPA | Transmission Equipment | [ASHE200909]:Hazy, smokey [MARN200908]: | [ASHE200909]:40s [MARN200908]: | [ASHE200909]:~220.4/224.4 mi from Ashe [MARN200908]:19.6 mi. | [ASHE200909]:Y [MARN200908]: | [Ops(MARN)200908]: Marion terminal equipment inspected. [Ops(ASHE)200909]: Ashe Marion #2 500kV line tripped to lockout. Fire and smoke in area outside of Marion, affecting numerous BPA lines. Terminal inspect of Ashe HV equipment including PCBs 4937 & 4940 found no issues. SEMM B phase evolving to a 3 phase fault FLAR 14.88 mi from Marion. [Spc(CHHQ)201007]: Evolving fault: BG fault >> hybrid trip start, B phase open >> CG fault (while hybrid trip timer was timing) >> 3-phase trip >> improper reclose >> ABC fault >> SOTF trip/lockout. Additional Trouble: the relay should not have reclosed after the 3-phase trip. SPC Branch investigated, correction made to reclose logic.
215854 | 124 |  | Buckley-Marion No 1 500kV line | L |  | 500 | CHE TDA TDW | TDA RED SAL | BPAT | 99.33 | 2020-09-08 01:52 | 2020-09-08 15:01 | 789 | Auto | Fire | BPA | Transmission Equipment | [MARN200908]: [BKLY200908]: | [MARN200908]: [BKLY200908]: | [MARN200908]: [BKLY200908]:90 miles | [MARN200908]: [BKLY200908]:Y | [Ops(MARN)200908]: Marion terminal equipment inspected. [Spc(*TDW)200930]: On 09/08/2020 at about 01:52 a C phase to A phase fault was detected on the Buckley – Marion line. The SEL-421 relay at Buckley substation detected the fault to be about 90 miles away from Buckley substation. Since the line is about 99.33 miles long that would place the fault about 90.6% of the way down the line from Buckley which places the fault outside of the zone 1 but still inside the zone 2 protection zone. Buckley sent a permissive trip signal and received a permissive and direct trip signal which caused the relays at Buckley to trip off the line at which point Buckley also sent a direct trip signal back. The PCBs appear to have opened in three cycles or less after receiving the trip signal. Since it was a multi-phase fault the breakers were tripped three pole. From the Buckley relays it appears as though the Marion side attempted to reclose but was unsuccessful so a reclose block signal was sent to the Buckley relays from the Marion Relays.
215859 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 01:52 | 2020-09-08 10:06 | 494 | Auto | Fire | BPA | Transmission Equipment | [MARN200908]: [JDAY200921]:UNKNOWN | [MARN200908]: [JDAY200921]:UNKNOWN | [MARN200908]: [JDAY200921]:128 | [MARN200908]: [JDAY200921]:Y | [Ops(MARN)200908]: Marion terminal equipment inspected. [Spc(CHHQ)200924]: Evolving fault: AG fault >> hybrid trip start, A-phase open >> BC fault >> 3ph trip
215853 | 1092 |  | Slatt tap to Ashe-Marion No 2 500kV line | T | G | 500 | ASH CHE | TRI | BPAT | 0.1 | 2020-09-08 01:52 | 2020-09-08 14:57 | 785 | Auto | Fire | BPA | Transmission Equipment | [ASHE200909]:Hazy, smokey [MARN200908]: | [ASHE200909]:40s [MARN200908]: | [ASHE200909]:~220.4/224.4 mi from Ashe [MARN200908]:19.6 mi. | [ASHE200909]:Y [MARN200908]: | [Ops(MARN)200908]: Marion terminal equipment inspected. [Ops(ASHE)200909]: Ashe Marion #2 500kV line tripped to lockout. Fire and smoke in area outside of Marion, affecting numerous BPA lines. Terminal inspect of Ashe HV equipment including PCBs 4937 & 4940 found no issues. SEMM B phase evolving to a 3 phase fault FLAR 14.88 mi from Marion. [Spc(CHHQ)201007]: Evolving fault: BG fault >> hybrid trip start, B phase open >> CG fault (while hybrid trip timer was timing) >> 3-phase trip >> improper reclose >> ABC fault >> SOTF trip/lockout. Additional Trouble: the relay should not have reclosed after the 3-phase trip. SPC Branch investigated, correction made to reclose logic.
215876 | 2578 |  | Buckley Station Service tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.01 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215876 | 2564 |  | Jones Canyon-Santiam No 1 230kV line | L | G | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 152.35 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215876 | 2575 |  | Jones Canyon-Tumble Creek section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 124.39 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215876 | 2579 |  | Tumble Creek tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.1 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215876 | 2580 |  | Tumble Creek-Santiam section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | SAL | BPAT | 27.96 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215877 | 272 | Consumers Power | Tumble Creek: Consumers Power 24.9kV Feeder 1 | P |  | 24.9 | CHE | SAL |  |  | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Unknown | BPA | Conductor/Hardware
215879 | 2578 |  | Buckley Station Service tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.01 | 2020-09-08 05:36 | 2020-09-19 21:55 | 16819 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215879 | 2564 |  | Jones Canyon-Santiam No 1 230kV line | L | G | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 152.35 | 2020-09-08 05:36 | 2020-09-19 22:13 | 16837 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215879 | 2575 |  | Jones Canyon-Tumble Creek section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 124.39 | 2020-09-08 05:36 | 2020-09-19 22:13 | 16837 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215879 | 2579 |  | Tumble Creek tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.1 | 2020-09-08 05:36 | 2020-09-10 12:28 | 3292 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215879 | 2580 |  | Tumble Creek-Santiam section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | SAL | BPAT | 27.96 | 2020-09-08 05:36 | 2020-09-10 12:28 | 3292 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215878 | 272 | Consumers Power | Tumble Creek: Consumers Power 24.9kV Feeder 1 | P |  | 24.9 | CHE | SAL |  |  | 2020-09-08 05:36 | 2020-09-10 12:28 | 3292 | Auto | Unknown | BPA | Conductor/Hardware
215896 | 32 |  | Ashe-Marion No 2 500kV line | L |  | 500 | ASH CHE | TRI TDA RED SAL | BPAT | 224.01 | 2020-09-08 19:47 | 2020-09-08 19:47 | 0 | Auto | Smoke | BPA | Transmission Equipment | [ASHE200909]:Hazy / Smokey [MARN200909]: | [ASHE200909]:80s [MARN200909]: | [ASHE200909]:~229.9/229.8 miles from Ashe by Relay [MARN200909]:22 mi. | [ASHE200909]:Y [MARN200909]:Y | [Disp200909]: FLAR SHOWS 21.7MILES FROM MARION, SEMM 'B' PHASE. [Ops(ASHE)200909]: Ashe - Marion #2 500kV line trip and reclosed. B phase to grd fault. Fire and smoke in the area outside Marion affecting numerous BPA lines. Terminal inspection of affected high voltage equipment at Ashe complete with no issues found. PCBs 4937 and 4940 at Ashe. [Ops(MARN)200909]: B-phase to ground fault with successful reclose. Marion terminal equipment inspected.
215896 | 1092 |  | Slatt tap to Ashe-Marion No 2 500kV line | T | G | 500 | ASH CHE | TRI | BPAT | 0.1 | 2020-09-08 19:47 | 2020-09-08 19:47 | 0 | Auto | Smoke | BPA | Transmission Equipment | [ASHE200909]:Hazy / Smokey [MARN200909]: | [ASHE200909]:80s [MARN200909]: | [ASHE200909]:~229.9/229.8 miles from Ashe by Relay [MARN200909]:22 mi. | [ASHE200909]:Y [MARN200909]:Y | [Disp200909]: FLAR SHOWS 21.7MILES FROM MARION, SEMM 'B' PHASE. [Ops(ASHE)200909]: Ashe - Marion #2 500kV line trip and reclosed. B phase to grd fault. Fire and smoke in the area outside Marion affecting numerous BPA lines. Terminal inspection of affected high voltage equipment at Ashe complete with no issues found. PCBs 4937 and 4940 at Ashe. [Ops(MARN)200909]: B-phase to ground fault with successful reclose. Marion terminal equipment inspected.
215899 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 20:02 | 2020-09-08 20:10 | 8 | Auto | Smoke | BPA | Transmission Equipment | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:130.1 | [MARN200909]: [JDAY201020]:Y | [Ops(MARN)200909]: This fault was masked , see ID 215901 [Spc(CHHQ)200924]: Evolving fault: BG fault >> hybrid trip >> reclose >> AB fault >> 3ph trip [TOps201213]: Spc(JDAY) Type of fault changed from 1 Line to Ground to 3 Phase per the Outage Review Team.
215900 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 20:12 | 2020-09-08 20:12 | 0 | Auto | Fire | BPA | Transmission Equipment | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:119.6 | [MARN200909]:Y [JDAY201020]:Y | [Disp200909]: OPERATOR REPORTS PHASE TO PHASE, 22 MILES FROM MARION. [Ops(MARN)200909]: This fault was masked by future fault, see ID 215901
215901 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 20:13 | 2020-09-09 13:45 | 1052 | Auto | Fire | BPA | Transmission Equipment | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]:15.71 - 21.71 miles [JDAY201020]:118 | [MARN200909]:Y [JDAY201020]:Y | [Disp200909]: OPERATOR REPORTS PHASE TO PHASE, 22 MILES FROM MARION. [Ops(MARN)200909]: Set 2 never produced any fault location data, while I was gathering data. [Spc(CHHQ)200924]: BG fault >> hybrid trip >> reclose (held ~7s) >> BG fault >> 3ph trip (TOPD = 900cyc) [Ops(JDAY)201020]: PCB 4170 TRIPPED, RECLOSED THEN LOCKED OUT PCB 4167 TRIPPED, RECL RELAY IS NORMALLY C/O

## Raw
Line and segments, Planned, Automatic from 9/5/2020 00:00 to 9/8/2020 23:59 for Transmission Lines Ashe-Marion No 2 500kV line, Big Cliff-Detroit PH No 1&2 13.8kV line, Buckley-Marion No 1 500kV line, Detroit-Santiam No 1 230kV line, John Day-Marion No 1 500kV line, Jones Canyon-Santiam No 1 230kV line, Ordered by LineName, out_datetime
Customer , Planned, Automatic from 9/5/2020 00:00 to 9/8/2020 23:59, Consumers Power Ordered by CustomerName, out_datetime
Outage ID | Tred ID | Customer Name | Transformer/Line/POD Name | Type | Gen Flag | kV | Ops Spc HQ | O&M District | Trans Owner NERC TADS | Length (Mi) | OutDatetime | InDatetime | Dur Mins | Auto Plan | Cause | Responsible System | Component | Weather | Temperature (F) | Fault Location | Dfr/Osc Operated | Comments
107973 | 32 |  | Ashe-Marion No 2 500kV line | L | T | 500 | ASH CHE | TRI TDA RED SAL | BPAT | 224.01 | 1988-01-01 11:00 |  | Still Out | Plan | Normally Out | BPA | [5 empty] | [TOps980305]: Added tap outage 3/5/98. This tap is normally open and is out. ALH
215853 | 32 |  | Ashe-Marion No 2 500kV line | L |  | 500 | ASH CHE | TRI TDA RED SAL | BPAT | 224.01 | 2020-09-08 01:52 | 2020-09-08 14:57 | 785 | Auto | Fire | BPA | Transmission Equipment | [ASHE200909]:Hazy, smokey [MARN200908]: | [ASHE200909]:40s [MARN200908]: | [ASHE200909]:~220.4/224.4 mi from Ashe [MARN200908]:19.6 mi. | [ASHE200909]:Y [MARN200908]: | [Ops(MARN)200908]: Marion terminal equipment inspected. [Ops(ASHE)200909]: Ashe Marion #2 500kV line tripped to lockout. Fire and smoke in area outside of Marion, affecting numerous BPA lines. Terminal inspect of Ashe HV equipment including PCBs 4937 & 4940 found no issues. SEMM B phase evolving to a 3 phase fault FLAR 14.88 mi from Marion. [Spc(CHHQ)201007]: Evolving fault: BG fault >> hybrid trip start, B phase open >> CG fault (while hybrid trip timer was timing) >> 3-phase trip >> improper reclose >> ABC fault >> SOTF trip/lockout. Additional Trouble: the relay should not have reclosed after the 3-phase trip. SPC Branch investigated, correction made to reclose logic.
215896 | 32 |  | Ashe-Marion No 2 500kV line | L |  | 500 | ASH CHE | TRI TDA RED SAL | BPAT | 224.01 | 2020-09-08 19:47 | 2020-09-08 19:47 | 0 | Auto | Smoke | BPA | Transmission Equipment | [ASHE200909]:Hazy / Smokey [MARN200909]: | [ASHE200909]:80s [MARN200909]: | [ASHE200909]:~229.9/229.8 miles from Ashe by Relay [MARN200909]:22 mi. | [ASHE200909]:Y [MARN200909]:Y | [Disp200909]: FLAR SHOWS 21.7MILES FROM MARION, SEMM 'B' PHASE. [Ops(ASHE)200909]: Ashe - Marion #2 500kV line trip and reclosed. B phase to grd fault. Fire and smoke in the area outside Marion affecting numerous BPA lines. Terminal inspection of affected high voltage equipment at Ashe complete with no issues found. PCBs 4937 and 4940 at Ashe. [Ops(MARN)200909]: B-phase to ground fault with successful reclose. Marion terminal equipment inspected.
215928 | 485 |  | Big Cliff-Detroit PH No 1&2 13.8kV line | L |  | 13.8 | CHE | SAL | BPAT | 5.66 | 2020-09-08 00:19 | 2020-09-10 15:45 | 3806 | Auto | Forced (Configuration) | BPA
215876 | 2578 |  | Buckley Station Service tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.01 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215879 | 2578 |  | Buckley Station Service tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.01 | 2020-09-08 05:36 | 2020-09-19 21:55 | 16819 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215854 | 124 |  | Buckley-Marion No 1 500kV line | L |  | 500 | CHE TDA TDW | TDA RED SAL | BPAT | 99.33 | 2020-09-08 01:52 | 2020-09-08 15:01 | 789 | Auto | Fire | BPA | Transmission Equipment | [MARN200908]: [BKLY200908]: | [MARN200908]: [BKLY200908]: | [MARN200908]: [BKLY200908]:90 miles | [MARN200908]: [BKLY200908]:Y | [Ops(MARN)200908]: Marion terminal equipment inspected. [Spc(*TDW)200930]: On 09/08/2020 at about 01:52 a C phase to A phase fault was detected on the Buckley – Marion line. The SEL-421 relay at Buckley substation detected the fault to be about 90 miles away from Buckley substation. Since the line is about 99.33 miles long that would place the fault about 90.6% of the way down the line from Buckley which places the fault outside of the zone 1 but still inside the zone 2 protection zone. Buckley sent a permissive trip signal and received a permissive and direct trip signal which caused the relays at Buckley to trip off the line at which point Buckley also sent a direct trip signal back. The PCBs appear to have opened in three cycles or less after receiving the trip signal. Since it was a multi-phase fault the breakers were tripped three pole. From the Buckley relays it appears as though the Marion side attempted to reclose but was unsuccessful so a reclose block signal was sent to the Buckley relays from the Marion Relays.
215851 | 152 |  | Detroit-Santiam No 1 230kV line | L |  | 230 | CHE | SAL | BPAT | 22.8 | 2020-09-08 00:19 | 2020-09-10 15:45 | 3806 | Auto | Weather | BPA | Transmission Equipment | [DETR200914]: [SANT200909]: | [DETR200914]: [SANT200909]: | [DETR200914]: [SANT200909]: | [DETR200914]: [SANT200909]: | [Ops(SANT)200909]: No JM annunciator targets??? [Ops(DETR)200914]: The Detroit-Santiam #1 230KV Line tripped by relay action during wind/fire storm. Reclosing is normally cut-out at both terminals. line was patrolled by TLM, after finding nothing in line the line was reenergized successfully by MCC. This Line outage forced out both Detroit Power House 230KV Lines #1 & #2. [Spc(CHHQ)201105]: A-320 open at Detroit Sub (outage 215929). Santiam KDs detect BC fault and trip inst. Santiam DFR: Ib ~= Ic ~= 6200 Arms.
215859 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 01:52 | 2020-09-08 10:06 | 494 | Auto | Fire | BPA | Transmission Equipment | [MARN200908]: [JDAY200921]:UNKNOWN | [MARN200908]: [JDAY200921]:UNKNOWN | [MARN200908]: [JDAY200921]:128 | [MARN200908]: [JDAY200921]:Y | [Ops(MARN)200908]: Marion terminal equipment inspected. [Spc(CHHQ)200924]: Evolving fault: AG fault >> hybrid trip start, A-phase open >> BC fault >> 3ph trip
215899 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 20:02 | 2020-09-08 20:10 | 8 | Auto | Smoke | BPA | Transmission Equipment | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:130.1 | [MARN200909]: [JDAY201020]:Y | [Ops(MARN)200909]: This fault was masked , see ID 215901 [Spc(CHHQ)200924]: Evolving fault: BG fault >> hybrid trip >> reclose >> AB fault >> 3ph trip [TOps201213]: Spc(JDAY) Type of fault changed from 1 Line to Ground to 3 Phase per the Outage Review Team.
215900 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 20:12 | 2020-09-08 20:12 | 0 | Auto | Fire | BPA | Transmission Equipment | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:119.6 | [MARN200909]:Y [JDAY201020]:Y | [Disp200909]: OPERATOR REPORTS PHASE TO PHASE, 22 MILES FROM MARION. [Ops(MARN)200909]: This fault was masked by future fault, see ID 215901
215901 | 145 |  | John Day-Marion No 1 500kV line | L |  | 500 | CHE TDA TDE | TDA RED SAL | BPAT | 127.51 | 2020-09-08 20:13 | 2020-09-09 13:45 | 1052 | Auto | Fire | BPA | Transmission Equipment | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]: [JDAY201020]:UNKNOWN | [MARN200909]:15.71 - 21.71 miles [JDAY201020]:118 | [MARN200909]:Y [JDAY201020]:Y | [Disp200909]: OPERATOR REPORTS PHASE TO PHASE, 22 MILES FROM MARION. [Ops(MARN)200909]: Set 2 never produced any fault location data, while I was gathering data. [Spc(CHHQ)200924]: BG fault >> hybrid trip >> reclose (held ~7s) >> BG fault >> 3ph trip (TOPD = 900cyc) [Ops(JDAY)201020]: PCB 4170 TRIPPED, RECLOSED THEN LOCKED OUT PCB 4167 TRIPPED, RECL RELAY IS NORMALLY C/O
215876 | 2564 |  | Jones Canyon-Santiam No 1 230kV line | L | G | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 152.35 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215879 | 2564 |  | Jones Canyon-Santiam No 1 230kV line | L | G | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 152.35 | 2020-09-08 05:36 | 2020-09-19 22:13 | 16837 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215876 | 2575 |  | Jones Canyon-Tumble Creek section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 124.39 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215879 | 2575 |  | Jones Canyon-Tumble Creek section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | TRI TDA RED SAL | BPAT | 124.39 | 2020-09-08 05:36 | 2020-09-19 22:13 | 16837 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
107973 | 1092 |  | Slatt tap to Ashe-Marion No 2 500kV line | T |  | 500 | ASH CHE | TRI | BPAT | 0.1 | 1988-01-01 11:00 |  | Still Out | Plan | Normally Out | BPA | [5 empty] | [TOps980305]: Added tap outage 3/5/98. This tap is normally open and is out. ALH
215853 | 1092 |  | Slatt tap to Ashe-Marion No 2 500kV line | T | G | 500 | ASH CHE | TRI | BPAT | 0.1 | 2020-09-08 01:52 | 2020-09-08 14:57 | 785 | Auto | Fire | BPA | Transmission Equipment | [ASHE200909]:Hazy, smokey [MARN200908]: | [ASHE200909]:40s [MARN200908]: | [ASHE200909]:~220.4/224.4 mi from Ashe [MARN200908]:19.6 mi. | [ASHE200909]:Y [MARN200908]: | [Ops(MARN)200908]: Marion terminal equipment inspected. [Ops(ASHE)200909]: Ashe Marion #2 500kV line tripped to lockout. Fire and smoke in area outside of Marion, affecting numerous BPA lines. Terminal inspect of Ashe HV equipment including PCBs 4937 & 4940 found no issues. SEMM B phase evolving to a 3 phase fault FLAR 14.88 mi from Marion. [Spc(CHHQ)201007]: Evolving fault: BG fault >> hybrid trip start, B phase open >> CG fault (while hybrid trip timer was timing) >> 3-phase trip >> improper reclose >> ABC fault >> SOTF trip/lockout. Additional Trouble: the relay should not have reclosed after the 3-phase trip. SPC Branch investigated, correction made to reclose logic.
215896 | 1092 |  | Slatt tap to Ashe-Marion No 2 500kV line | T | G | 500 | ASH CHE | TRI | BPAT | 0.1 | 2020-09-08 19:47 | 2020-09-08 19:47 | 0 | Auto | Smoke | BPA | Transmission Equipment | [ASHE200909]:Hazy / Smokey [MARN200909]: | [ASHE200909]:80s [MARN200909]: | [ASHE200909]:~229.9/229.8 miles from Ashe by Relay [MARN200909]:22 mi. | [ASHE200909]:Y [MARN200909]:Y | [Disp200909]: FLAR SHOWS 21.7MILES FROM MARION, SEMM 'B' PHASE. [Ops(ASHE)200909]: Ashe - Marion #2 500kV line trip and reclosed. B phase to grd fault. Fire and smoke in the area outside Marion affecting numerous BPA lines. Terminal inspection of affected high voltage equipment at Ashe complete with no issues found. PCBs 4937 and 4940 at Ashe. [Ops(MARN)200909]: B-phase to ground fault with successful reclose. Marion terminal equipment inspected.
215876 | 2579 |  | Tumble Creek tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.1 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215879 | 2579 |  | Tumble Creek tap to Jones Canyon-Santiam No 1 230kV line | T |  | 230 | CHE MCN | SAL | BPAT | 0.1 | 2020-09-08 05:36 | 2020-09-10 12:28 | 3292 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215876 | 2580 |  | Tumble Creek-Santiam section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | SAL | BPAT | 27.96 | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:140 | [SANT200909]:Y [JCSB200910]: | [Ops(SANT)200909]: Appeared to be a successful reclose. equipment inspected. [Ops(JCSB)200910]: One operation with successful reclose. All terminal equipment inspected and appears normal.
215879 | 2580 |  | Tumble Creek-Santiam section of Jones Canyon-Santiam No 1 230kV line | S |  | 230 | CHE MCN | SAL | BPAT | 27.96 | 2020-09-08 05:36 | 2020-09-10 12:28 | 3292 | Auto | Fire | BPA | Transmission Equipment | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]: | [SANT200909]: [JCSB200910]:143 | [SANT200909]: [JCSB200910]: | [Ops(SANT)200909]: Multi phase fault with unsuccessful reclose. Equipment inspected. [Ops(JCSB)200910]: Multi phase fault, unsuccessful reclose. All terminal equipment inspected and appears normal. [Spc(CHHQ)201105]: Two faults within 10s in close proximity. 1st fault: initiated at 05:36:25.662, location = 136.7 miles (FLAR), ABC (~4800A/phase), proper 3-phase trip, proper TT, successful reclose (held for ~3.5s), instantaneous trip, proper RAS. 2nd fault: initiated at 05:36:34.013, location = 135.4 miles (FLAR), BC (~4300A/phase), proper 3-phase trip, proper TT, failed to reclose (reclose was blocked because it was within the 15s reset interval of the last reclose), instantaneous trip, proper RAS. FLAR puts these faults on the Santiam-Tumble Creek section of the line, which was successfully restored to service on 09-10 at 1228. There were no repairs to this section of line or trees removed from this section of line before restoration. The Tumble Creek-Jones Canyon section remained out until 09-19 at 2155. TLM located and removed a tree on this section at 123/1, approximately 121.2 miles from Jones-Canyon. [TOps201125]: Spc(SANT) Cause changed from Unknown to Fire per the Outage Review Team.
215819 | 275 | Consumers Power | Santiam: Consumers Power 69kV Feeder 1 | P |  | 69 | CHE | SAL |  |  | 2020-09-07 19:33 | 2020-09-09 12:27 | 2454 | Auto | Wind | Customer | Conductor/Hardware |  |  |  |  | [Ops(SANT)200909]: Reclosing was cut-out days earlier at CPI Dispatcher request - Red Flag Warning.
215877 | 272 | Consumers Power | Tumble Creek: Consumers Power 24.9kV Feeder 1 | P |  | 24.9 | CHE | SAL |  |  | 2020-09-08 05:27 | 2020-09-08 05:27 | 0 | Auto | Unknown | BPA | Conductor/Hardware
215878 | 272 | Consumers Power | Tumble Creek: Consumers Power 24.9kV Feeder 1 | P |  | 24.9 | CHE | SAL |  |  | 2020-09-08 05:36 | 2020-09-10 12:28 | 3292 | Auto | Unknown | BPA | Conductor/Hardware

## Notes
Adjustments to Report from Raw data extract from OARS
1 | Removed POD outages other than Tumble Creek: Consumers Power 24.9kV Feeder 1; change report header accordingly.
2 | Sort file by OutDatetime, remove sort order from report header.
3 | Adjust column widths
4 | Add "(Pacific Prevailing Time)" to Out and In Datetimes for clarity
BPA does not record outages to the Tumble Creek-Hall Ridge No 1 2.4kV line.